## Indices
PLEXOS technology | WEO_tech | Object_type | Operating_class | Mapping to NREL cost data | Mapping to DEA data | Fuel | Cofiring1 | Cofiring2 | PerformanceVar | CHPtypeETP | CCStype | FUELsub | FUELsimp | VRE | InertiaLOW | InertiaHI | StorageDuration | Category | CategorySub | StackCategory | FUELgas | FDtech | Fuel4 | Fuel5 | VRE2 | VRE3 | CategoryWEO | FlexCategory | CapacityCategory | QuickStart | Type | ScaleCat | VREsepcats | ScaleCatCHP | ScaleCat2 | CategoryCapacity | RegSplitCat | merge | MaxCap | HR | MSL_Inflex | MSL | MSL_Flex | RR | RR_Flex | RR_Inflex | RUR | RUR_Flex | RUR_Inflex | StorageVol | StartCost_hot | StartCost_warm | StartCost_cold | CoolingBand_hot | CoolingBand_warm | CoolingBand_cold | StartCost_single | MUT | MDT | RampCost | VOM | FOM | AuxDemand | POR | MTTR_POR | FFOR | MTTR_FFOR | PFOR | MTTR_PFOR | PFOR_Derating | DeratedMaintenance | FirmCapacity | CAPEX | ChargeEff | DischargeEff | RatingFactor | MaxCapFacDay
Battery_distributed | Battery4H | Battery | Battery | Battery | Batteries |  |  |  | 1 | nonCHP | Battery | Battery | Battery | Battery | 0 | 0 | 4 | Battery | Battery_distributed | Storage | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | No | Distributed | Battery | Battery | Battery | Battery | Battery | Battery | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 90 | 90 | #N/A | #N/A
Battery_utility_1h | Battery1HR | Battery | Battery | Battery | Batteries |  |  |  | 1 | nonCHP | Battery | Battery | Battery | Battery | 0 | 0 | 1 | Battery | Battery_utility | Storage | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | No | Utility | Battery | Battery | Battery | Battery | Battery | Battery | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 90 | 90 | #N/A | #N/A
Battery_utility_2h | Battery2HR | Battery | Battery | Battery | Batteries |  |  |  | 1 | nonCHP | Battery | Battery | Battery | Battery | 0 | 0 | 2 | Battery | Battery_utility | Storage | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | No | Utility | Battery | Battery | Battery | Battery | Battery | Battery | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 90 | 90 | #N/A | #N/A
Battery_utility_4h | Battery4HR | Battery | Battery | Battery | Batteries |  |  |  | 1 | nonCHP | Battery | Battery | Battery | Battery | 0 | 0 | 4 | Battery | Battery_utility | Storage | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | No | Utility | Battery | Battery | Battery | Battery | Battery | Battery | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 90 | 90 | #N/A | #N/A
Battery_utility_8h | Battery8HR | Battery | Battery | Battery | Batteries |  |  |  | 1 | nonCHP | Battery | Battery | Battery | Battery | 0 | 0 | 8 | Battery | Battery_utility | Storage | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | Battery | No | Utility | Battery | Battery | Battery | Battery | Battery | Battery | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | 0 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 90 | 90 | #N/A | #N/A
Biogases | Biogases | Generator | OCGT | Biomass | OCGT | Biogas |  |  | 1 | nonCHP | Bioenergy | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | None | RES | Other | Non-VRE | Non-VRE | Bioenergy | Dispatchable | Bioenergy | No | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | Biogases | 1 | 400 | 9.1162 | 50 | 20 | 10 | 10 | 20 | 8 | 9 | 18 | 7.2 | #N/A | 32 | 126 | 103 | 1 | 1 | 24 | 0 | 1 | 1 | 2.9444 | 7 | 12 | 0.96 | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 99.1781 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Biomass_CHP_Medium | Biomass CHP Medium | Generator | CHP Other | Biomass | CHP Other | Biomass |  |  | 1 | DH | Bioenergy | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | None | RES | Other | Non-VRE | Non-VRE | Bioenergy | Constrained | Bioenergy | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | Biomass CHP Medium | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Biomass_CHP_Small | Biomass CHP Small | Generator | CHP Other | Biomass | CHP Other | Biomass |  |  | 1 | Industrial | Bioenergy | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | None | RES | Other | Non-VRE | Non-VRE | Bioenergy | Constrained | Bioenergy | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | Biomass CHP Small | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Biomass_IGCC_with_CCS | Biomass IGCC with CCS | Generator | IGCC | Biomass | CCS - IGCC | Biomass |  |  | 1 | nonCHP | Bioenergy CCS | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | None | RES | Other | Non-VRE | Non-VRE | Bioenergy | Dispatchable | Bioenergy | No | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | Biomass IGCC with CCS | 1 | 800 | 10.9091 | 50 | 50 | 20 | 2.75 | 3 | 1.5 | 2.475 | 2.7 | 1.35 | #N/A | 54 | 64 | 104 | 1 | 3 | 100 | 0 | 8 | 8 | 3.2667 | 5.3 | 8.9 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 950 | #N/A | #N/A | #N/A | #N/A
Biomass_Power_Plant | Biomass Power Plant | Generator | Biomass dispatchable | Biomass | Biomass power plant (small) | Biomass |  |  | 1 | nonCHP | Bioenergy | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | None | RES | Other | Non-VRE | Non-VRE | Bioenergy | Dispatchable | Bioenergy | No | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | Biomass Power Plant | 1 | #N/A | 9.9828 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.043 | 47.6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2000 | #N/A | #N/A | 60 | #N/A
Coal_CCS | NEW CCS Coal | Generator | CCGT | CCGT | CCS - CCGT | Gas |  |  | 1 | nonCHP | Gas CCS | Gas-CCGT | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | CCGT | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_CCGT | Dispatchable | Gas_CCGT | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Gas | CCS CCGT 1 | 1 | 600 | 10.9091 | 50 | 45 | 15 | 3 | 20 | 2 | 2.7 | 18 | 1.8 | #N/A | 35 | 55 | 79 | 1 | 3 | 80 | 0 | 4 | 4 | 1.6 | 1.2 | 9 | 0.96 | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 94.5205 | #N/A | 1150 | #N/A | #N/A | #N/A | #N/A
Coal_CHP | CHP Coal | Generator | CHP Coal | Coal | CHP Coal | Bituminous coal |  |  | 1 | DH | Coal | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_IGCC | Dispatchable | Coal_IGCC | No | Dispatchable | Fossil | Fossil | Fossil_CHP | Fossil_plus | Fossil_CHP | CHP Coal | 1 | 100 | 10.2116 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 2.5 | 50 | 6 | 20 | 30 | 94 | 0.4 | #N/A | #N/A | #N/A | #N/A | #N/A
Coal_IGCC | Coal IGCC 1 | Generator | IGCC | IGCC | CCS - IGCC | Bituminous coal |  |  | 1 | nonCHP | Coal | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_IGCC | Dispatchable | Coal_IGCC | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | Coal IGCC 1 | 1 | 800 | 8.3721 | 50 | 50 | 20 | 2.75 | 3 | 1.5 | 2.475 | 2.7 | 1.35 | #N/A | 54 | 64 | 104 | 1 | 3 | 100 | 0 | 8 | 8 | 3.2667 | 5.3 | 8.9 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 950 | #N/A | #N/A | #N/A | #N/A
Coal_IGCC_CCS | CCS IGCC 1 | Generator | IGCC | IGCC CCS | CCS - IGCC | Bituminous coal |  |  | 1 | nonCHP | Coal CCS | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_IGCC | Dispatchable | Coal_IGCC | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | CCS IGCC 1 | 1 | 800 | 10.9091 | 50 | 50 | 20 | 2.75 | 3 | 1.5 | 2.475 | 2.7 | 1.35 | #N/A | 54 | 64 | 104 | 1 | 3 | 100 | 0 | 8 | 8 | 3.2667 | 5.3 | 8.9 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 950 | #N/A | #N/A | #N/A | #N/A
Coal_Oxyfuel_CCS | CCS Oxyfuel 1 | Generator | Coal supercritical | Coal CCS | CCS - Supercritical coal | Bituminous coal |  |  | 1 | nonCHP | Coal CCS | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_Supercritical | Dispatchable | Coal_Supercritical | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | CCS Oxyfuel 1 | 1 | 800 | 10.9091 | 50 | 25 | 20 | 2.75 | 4 | 1.5 | 2.475 | 3.6 | 1.35 | #N/A | 54 | 64 | 104 | 2 | 4 | 50 | 0 | 8 | 8 | 3.2667 | 3.1 | 41.8 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 1950 | #N/A | #N/A | #N/A | #N/A
Coal_Subcritical_Hard | Coal Subcritical 3 | Generator | Coal subcritical | Coal | Coal Subcritical | Bituminous coal |  |  | 1 | ex-CHP | Coal | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_Subcritical | Dispatchable | Coal_Subcritical | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | Coal Subcritical 3 | 1 | 800 | 11.1273 | 60 | 30 | 10 | 2.75 | 3.5 | 1.5 | 2.475 | 3.15 | 1.35 | #N/A | 54 | 64 | 104 | 2 | 4 | 110 | 0 | 8 | 8 | 3.5 | 0.125 | 45.3 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 1650 | #N/A | #N/A | #N/A | #N/A
Coal_Subcritical_Lignite | Coal Subcritical 1 | Generator | Coal lignite | Lignite | Coal Subcritical | Lignite |  |  | 1 | nonCHP | Coal | Lignite | Lignite | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_Subcritical | Dispatchable | Coal_Subcritical | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | Coal Subcritical 1 | 1 | 800 | 11.3784 | 60 | 30 | 30 | 1.5 | 3.5 | 1 | 1.35 | 3.15 | 0.9 | #N/A | 54 | 64 | 104 | 2 | 4 | 110 | 0 | 8 | 8 | 3.5 | 0.125 | 45.3 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 1650 | #N/A | #N/A | #N/A | #N/A
Coal_Supercritical | Coal Supercritical 1 | Generator | Coal supercritical | Coal | CCS - Supercritical coal | Bituminous coal |  |  | 1 | nonCHP | Coal | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_IGCC | Dispatchable | Coal_IGCC | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | Coal Supercritical 1 | 1 | 800 | 13.8462 | 50 | 25 | 20 | 2.75 | 4 | 1.5 | 2.475 | 3.6 | 1.35 | #N/A | 54 | 64 | 104 | 2 | 4 | 50 | 0 | 8 | 8 | 3.2667 | 3.1 | 41.8 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 1950 | #N/A | #N/A | #N/A | #N/A
Coal_Ultrasupercritical | Coal Ultrasupercritical 1 | Generator | Coal ultrasupercritical | Coal | Coal Ultra supercritical | Bituminous coal |  |  | 1 | nonCHP | Coal | Bituminous coal | Bituminous coal | Non-VRE | 2 | 4 |  | Coal | Coal | Coal | Coal | Thermal | Thermal | Coal | Non-VRE | Non-VRE | Coal_Supercritical | Dispatchable | Coal_Supercritical | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Coal | Coal Ultrasupercritical 1 | 1 | 800 | 8.1818 | 50 | 30 | 20 | 2.75 | 5 | 1.5 | 2.475 | 4.5 | 1.35 | #N/A | 54 | 64 | 104 | 2 | 4 | 50 | 0 | 8 | 8 | 3.2667 | 0.11 | 56.6 | 0.94 | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 91.7808 | #N/A | 1524.8 | #N/A | #N/A | #N/A | #N/A
Fuel_cell | Fuel Cell 1 | Generator | OCGT | OCGT | OCGT | Gas |  |  | 1 | nonCHP | Fuel Cell | Fuel Cell | Fuel Cell | Non-VRE | 2 | 4 |  | Gas | Gas | Fuel Cell | Fuel Cell | Thermal | RES | Other | VRE | VRE | Fuel_cell | Dispatchable | Fuel_cell | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Fuel Cell | Fuel Cell 1 | 1 | 400 | 12 | 50 | 20 | 10 | 10 | 20 | 8 | 9 | 18 | 7.2 | #N/A | 32 | 126 | 103 | 1 | 1 | 24 | 0 | 1 | 1 | 2.9444 | 7 | 12 | 0.96 | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 99.1781 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Gas_CCGT | Gas CCGT 1 | Generator | CCGT | CCGT | CCS - CCGT | Gas |  |  | 1 | nonCHP | Gas | Gas-CCGT | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | CCGT | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_CCGT | Dispatchable | Gas_CCGT | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Gas | Gas CCGT 1 | 1 | 600 | 8.9778 | 50 | 45 | 15 | 3 | 20 | 2 | 2.7 | 18 | 1.8 | #N/A | 35 | 55 | 79 | 1 | 3 | 80 | 0 | 4 | 4 | 1.6 | 1.2 | 9 | 0.96 | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 94.5205 | #N/A | 1150 | #N/A | #N/A | #N/A | #N/A
Gas_CCGT_CCS | NEW CCS Gas CCGT | Generator | CCGT | CCGT CCS | CCS - CCGT | Gas |  |  | 1 | nonCHP | Gas CCS | Gas-CCGT | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | CCGT | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_CCGT | Dispatchable | Gas_CCGT | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Gas | NEW CCS Gas CCGT | 1 | 600 | 16.3636 | 50 | 45 | 15 | 3 | 20 | 2 | 2.7 | 18 | 1.8 | #N/A | 35 | 55 | 79 | 1 | 3 | 80 | 0 | 4 | 4 | 1.6 | 1.2 | 9 | 0.96 | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 94.5205 | #N/A | 1150 | #N/A | #N/A | #N/A | #N/A
Gas_CCGT_CHP_CCS | NEW CCS Gas CCGT CHP MaxMin | Generator | CHP Gas | CCGT CCS | CCS - CCGT | Gas |  |  | 1 | Industrial | Gas CCS | Gas-CCGT | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | CHP | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_CCGT | Dispatchable | Gas_CCGT | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Gas | NEW CCS Gas CCGT CHP MaxMin | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.2 | 9 | 0.96 | 6 | 360 | 2 | 30 | 1 | 27 | 30 | 94 | 0.4 | 1150 | #N/A | #N/A | #N/A | #N/A
Gas_CHP | NEW CHP Gas | Generator | CHP Gas | OCGT | OCGT | Gas |  |  | 1 | Industrial | Gas | Gas-OCGT | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | OCGT | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_GT | Dispatchable | Gas_GT | Yes | Dispatchable | Fossil | Fossil | Fossil_CHP | Fossil_plus | Fossil_CHP | NEW CHP Gas | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.96 | 6 | 360 | 2 | 30 | 1 | 27 | 30 | 94 | 0.4 | #N/A | #N/A | #N/A | #N/A | #N/A
Gas_GT | Gas GT 1 | Generator | OCGT | OCGT | OCGT | Gas |  |  | 1 | nonCHP | Gas | Gas-OCGT | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | OCGT | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_GT | Dispatchable | Gas_GT | Yes | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Gas | Gas GT 1 | 1 | 400 | 13.8771 | 50 | 20 | 10 | 10 | 20 | 8 | 9 | 18 | 7.2 | #N/A | 32 | 126 | 103 | 1 | 1 | 24 | 0 | 1 | 1 | 2.9444 | 7 | 12 | 0.96 | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 99.1781 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Gas_Steam | Gas Steam 1 | Generator | Steam turbine (Gas/Oil) | OCGT | Steam turbine (Gas/Oil) | Gas |  |  | 1 | nonCHP | Gas | Gas-steam | Gas | Non-VRE | 4 | 6 |  | Gas | Gas | Gas | Thermal_gas | Thermal | Thermal | Gas | Non-VRE | Non-VRE | Gas_steam | Dispatchable | Gas_steam | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Gas | Gas Steam 1 | 1 | 600 | 13.5115 | 50 | 45 | 20 | 3 | 20 | 2 | 2.7 | 18 | 1.8 | #N/A | 36 | 58 | 75 | 2 | 4 | 80 | 0 | 8 | 8 | 3 | 7 | 12 | 0.96 | 8.2192 | 360 | 2 | 30 | 1 | 27 | 40 | 91.7808 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Geothermal | Geothermal Elec | Generator | Geothermal | Geothermal | Geothermal |  |  |  | 1 | nonCHP | Geothermal | Geothermal | Geothermal | Non-VRE | 0 | 0 |  | Geothermal | Geothermal | Geothermal | Geothermal | Thermal | RES | Other | Non-VRE | Non-VRE | Geothermal | Constrained | Geothermal | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Geothermal | Geothermal Elec | 1 | 55 | #N/A | #N/A | #N/A | #N/A | 2.75 | 3.5 | 1.5 | 2.475 | 3.15 | 1.35 | #N/A | 54 | 64 | 104 | 2 | 4 | 110 | 0 | 4 | 4 | 3.2667 | 0 | 131 | 0.94 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.8 | #N/A | #N/A | #N/A | 80 | #N/A
Geothermal_CHP | Geothermal CHP | Generator | CHP Other | Geothermal | CHP Other |  |  |  | 1 | DH | Geothermal | Geothermal | Geothermal | Non-VRE | 0 | 0 |  | Geothermal | Geothermal | Geothermal | Geothermal | Thermal | RES | Other | Non-VRE | Non-VRE | Geothermal | Constrained | Geothermal | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Geothermal | Geothermal CHP | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | 80 | #N/A
Hydro_PSH | Hydro PSH | Generator | Hydro PSH | PSH | Hydro pumped storage |  |  |  | 1 | nonCHP | Hydro | Hydro | Hydro | Non-VRE | 2 | 4 | 10 | Hydro | Hydro | Hydro | Storage | Hydro | Hydro | Hydro | Non-VRE | Non-VRE | Hydro | Pump | Hydro | Yes | Pump | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Hydro | Hydro PSH | 1 | 250 | #N/A | 33 | 33 | 0 | 50 | 50 | 0 | #N/A | #N/A | #N/A | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 1.325 | 8 | 0.99 | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 98.0822 | #N/A | 860 | 75 | 100 | #N/A | #N/A
Hydro_Pumpback_PSH | Hydro Pumpback PSH | Generator | Hydro_Pumpback_PSH | PSH | Hydro pumped storage |  |  |  | 1 | nonCHP | Hydro | Hydro | Hydro | Non-VRE | 2 | 4 | 10 | Hydro | Hydro | Hydro | Storage | Hydro | Hydro | Hydro | Non-VRE | Non-VRE | Hydro | Pump | Hydro | Yes | Pump | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Hydro | Hydro Pumpback PSH | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 12 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1.325 | 8 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 860 | 75 | 100 | #N/A | #N/A
Hydro_Reservoir | Hydro Reservoir | Generator | Hydro Reservoir | Hydro | Large hydro power plant |  |  |  | 1 | nonCHP | Hydro | Hydro | Hydro | Non-VRE | 2 | 4 |  | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Non-VRE | Non-VRE | Hydro | Dispatchable | Hydro | Yes | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Hydro | Hydro Reservoir | 1 | 150 | #N/A | 0 | 0 | 0 | 50 | 50 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0.65 | 37.7 | 0.99 | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 98.0822 | 0.35885 | 2080 | #N/A | #N/A | 35.8846 | #N/A
Hydro_RoR | Hydro RoR | Generator | Hydro RoR | Hydro | Mini-micro hydro power plant |  |  |  | 1 | nonCHP | Hydro | Hydro | Hydro | Non-VRE | 2 | 4 |  | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Non-VRE | Non-VRE | Hydro | Constrained | Hydro | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Hydro | Hydro RoR | 1 | 5 | #N/A | 0 | 0 | 0 | #N/A | #N/A | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0.5 | 53 | 0.99 | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 98.0822 | 0.75885 | 2700 | #N/A | #N/A | 75.8846 | #N/A
Hydro_RoRpondage | Hydro RoRpondage | Generator | Hydro RoRpondage | Hydro | Medium-small hydro power plant |  |  |  | 1 | nonCHP | Hydro | Hydro | Hydro | Non-VRE | 2 | 4 |  | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Hydro | Non-VRE | Non-VRE | Hydro | Dispatchable | Hydro | Yes | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Hydro | Hydro RoRpondage | 1 | 50 | #N/A | 0 | 0 | 0 | 50 | 50 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0.5 | 41.9 | 0.99 | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 98.0822 | 0.75885 | 2290 | #N/A | #N/A | 75.8846 | 75.8846
Marine | Tide And Wave | Generator | Ocean energy | Ocean energy | Tidal Stream |  |  |  | 1 | nonCHP | Marine | Ocean | Ocean | Non-VRE | 0 | 0 |  | Other RE | Marine | Other | Ocean | Marine | RES | Other | Ocean | Ocean | Marine | Constrained | Marine | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Marine | Tide And Wave | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 11.7257 | 283 | 0.99 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.33 | 5300 | #N/A | #N/A | 33 | #N/A
Nuclear | Nuclear 1 | Generator | Nuclear | Nuclear | Nuclear | Uranium |  |  | 1 | nonCHP | Nuclear | Uranium | Uranium | Non-VRE | 2 | 4 |  | Nuclear | Nuclear | Nuclear | Nuclear | Nuclear | Nuclear | Nuclear | Non-VRE | Non-VRE | Nuclear | Dispatchable | Nuclear | No | Dispatchable | Nuclear | Nuclear | Nuclear | Fossil_plus | Nuclear | Nuclear 1 | 1 | 1000 | #N/A | 50 | 40 | 30 | 0.5 | 3 | 0.5 | 0.45 | 2.7 | 0.45 | #N/A | 162 | 192 | 312 | 2 | 4 | 330 | 0 | 120 | 120 | 3.2667 | 2 | 99 | 0.94 | 0.10959 | 960 | 2.5 | 50 | 6 | 20 | 30 | 99.8904 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Nuclear_CHP | CHP Nuclear | Generator | CHP Other | Nuclear | CHP Other | Uranium |  |  | 1 | DH | Nuclear | Uranium | Uranium | Non-VRE | 2 | 4 |  | Nuclear | Nuclear | Nuclear | Nuclear | Nuclear | Nuclear | Nuclear | Non-VRE | Non-VRE | Nuclear | Constrained | Nuclear | No | Constrained | Nuclear | Nuclear | Nuclear | Fossil_plus | Nuclear | CHP Nuclear | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Oil_CHP | CHP Oil | Generator | CHP Oil | OCGT | Steam turbine (Gas/Oil) | Oil |  |  | 1 | DH | Oil | Oil | Oil | Non-VRE | 2 | 4 |  | Oil | Oil | Oil | Oil | Thermal | Thermal | Oil | Non-VRE | Non-VRE | Oil | Constrained | Oil | Yes | Constrained | Fossil | Fossil | Fossil_CHP | Fossil_plus | Fossil_CHP | CHP Oil | 1 | 5 | 12.8599 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.96 | 6 | 360 | 2 | 30 | 1 | 27 | 30 | 94 | 0.4 | #N/A | #N/A | #N/A | #N/A | #N/A
Oil_GT | Oil GT 1 | Generator | OCGT | OCGT | OCGT | Oil |  |  | 1 | nonCHP | Oil | Oil | Oil | Non-VRE | 2 | 4 |  | Oil | Oil | Oil | Oil | Thermal | Thermal | Oil | Non-VRE | Non-VRE | Oil | Dispatchable | Oil | Yes | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Oil | Oil GT 1 | 1 | 400 | 15.4799 | 50 | 20 | 10 | 10 | 20 | 8 | 9 | 18 | 7.2 | #N/A | 32 | 126 | 103 | 1 | 1 | 24 | 0 | 1 | 1 | 2.9444 | 7 | 12 | 0.96 | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 99.1781 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Oil_Steam | Oil Steam 1 | Generator | Steam turbine (Gas/Oil) | OCGT | Steam turbine (Gas/Oil) | Oil |  |  | 1 | nonCHP | Oil | Oil | Oil | Non-VRE | 4 | 6 |  | Oil | Oil | Oil | Oil | Thermal | Thermal | Oil | Non-VRE | Non-VRE | Oil | Dispatchable | Oil | No | Dispatchable | Fossil | Fossil | Fossil | Fossil_plus | Oil | Oil Steam 1 | 1 | 600 | 15.4467 | 50 | 45 | 20 | 3 | 20 | 2 | 2.7 | 18 | 1.8 | #N/A | 36 | 58 | 75 | 2 | 4 | 80 | 0 | 8 | 8 | 3 | 7 | 12 | 0.96 | 8.2192 | 360 | 2 | 30 | 1 | 27 | 40 | 91.7808 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Solar_CSP | Solar CSP | Generator | Solar CSP | Solar CSP | Solar CSP |  |  |  | 1 | nonCHP | Solar | Solar | Solar | Non-VRE | 0 | 0 |  | Solar | Solar | Solar | Solar | Solar | RES | Other | Non-VRE | Non-VRE | ConcentratedSolarPower | Dispatchable | ConcentratedSolarPower | No | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Solar | Solar CSP | 1 | 100 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 4.1 | 67 | 0.97 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.34 | #N/A | #N/A | #N/A | 34 | 34
Solar_CSP_CHP | CHP Solar | Generator | CHP Other | Solar CSP | CHP Other |  |  |  | 1 | DH | Solar | Solar | Solar | Non-VRE | 0 | 0 |  | Solar | Solar | Solar | Solar | Solar | CHP | Other | Non-VRE | Non-VRE | ConcentratedSolarPower | Constrained | ConcentratedSolarPower | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Solar | CHP Solar | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | 34 | 34
Solar_PV_Buildings | Solar PV Buildings | Generator | Solar PV Buildings | Solar PV Buildings | Rooftop PV |  |  |  | 1 | nonCHP | Solar | Solar | Solar | VRE | 0 | 0 |  | Solar | Solar_PV_Buildings | Solar | Solar | Solar | RES | SolarPV | Solar | Solar | SolarPV | VRE | SolarPV | No | VRE | Solar | Solar_buildings | Solar | Solar | Solar | Solar PV Buildings | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 14.4 | 0.99 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | #N/A | #N/A | 17.6941 | #N/A
Solar_PV_Utility | Solar PV Utility | Generator | Solar PV Utility | Solar PV Utility | Ground-mounted PV |  |  |  | 1 | nonCHP | Solar | Solar | Solar | VRE | 0 | 0 |  | Solar | Solar_PV_Utility | Solar | Solar | Solar | RES | SolarPV | Solar | Solar | SolarPV | VRE | SolarPV | No | VRE | Solar | Solar_utility | Solar | Solar | Solar | Solar PV Utility | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 14.4 | 0.99 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 0 | #N/A | #N/A | 19.4064 | #N/A
Waste | Waste to Energy | Generator | Solid biomass | Biomass | Solid biomass |  |  |  | 1 | nonCHP | Non-renewable waste | Non-renewable waste | Non-renewable waste | Non-VRE | 2 | 4 |  | Other | Non-renewable waste | Other | Non-renewable waste | Non-renewable waste | RES | Other | Non-VRE | Non-VRE | Bioenergy | Dispatchable | Bioenergy | No | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | Waste to Energy | 1 | 25 | 9.9828 | 30 | 30 | 25 | 2.75 | 3.5 | 1.5 | 2.475 | 3.15 | 1.35 | #N/A | 54 | 64 | 104 | 2 | 4 | 110 | 0 | 4 | 4 | 3.2667 | #N/A | #N/A | 0.94 | 8.2192 | 360 | 3 | 50 | 10 | 20 | 30 | 91.7808 | 0.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Waste_CHP | NEW CHP OtherSources | Generator | CHP Other | Biomass | CHP Other |  |  |  | 1 | Industrial | Non-renewable waste | Non-renewable waste | Non-renewable waste | Non-VRE | 2 | 4 |  | Other | Non-renewable waste | Other | Non-renewable waste | Non-renewable waste | RES | Other | Non-VRE | Non-VRE | Bioenergy | Constrained | Bioenergy | No | Constrained | Fossil | Fossil | Fossil_CHP | Fossil_plus | Fossil_CHP | NEW CHP OtherSources | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Waste_Renewable | NEW CHP BiomassandWaste | Generator | Renewable waste | Biomass | Biomass power plant (small) |  |  |  | 1 | Industrial | Bioenergy | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | Thermal | RES | Other | Non-VRE | Non-VRE | Bioenergy | Dispatchable | Bioenergy | No | Dispatchable | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | NEW CHP BiomassandWaste | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 3.043 | 47.6 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 2000 | #N/A | #N/A | 60 | #N/A
Waste_Renewable_CHP | NEW CHP BiomassandWaste | Generator | CHP Other | Biomass | CHP Other |  |  |  | 1 | Industrial | Bioenergy | Biomass | Biomass | Non-VRE | 2 | 4 |  | Bioenergy | Bioenergy | Bioenergy | Biomass | Thermal | RES | Other | Non-VRE | Non-VRE | Bioenergy | Constrained | Bioenergy | No | Constrained | Hydro_plus | Hydro_plus | Hydro_plus | Hydro_plus | Bioenergy | NEW CHP BiomassandWaste | 1 | 20 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.94 | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 94 | 0.6 | #N/A | #N/A | #N/A | #N/A | #N/A
Wind_Offshore | Wind Offshore | Generator | Wind offshore | Wind Offshore | Wind Offshore |  |  |  | 1 | nonCHP | Wind | Wind | Wind | VRE | 0 | 0 |  | Wind | Wind_Offshore | Wind | Wind | Wind | RES | Wind | Wind | Wind | Wind | VRE | Wind | No | VRE | Wind | Wind_offshore | Wind | Wind | Wind | Wind Offshore | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 5.5 | 72.6 | 0.99 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.47852 | 3500 | #N/A | #N/A | 47.8523 | #N/A
Wind_Onshore | Wind Onshore | Generator | Wind onshore | Wind Onshore | Wind Onshore |  |  |  | 1 | nonCHP | Wind | Wind | Wind | VRE | 0 | 0 |  | Wind | Wind_Onshore | Wind | Wind | Wind | RES | Wind | Wind | Wind | Wind | VRE | Wind | No | VRE | Wind | Wind_onshore | Wind | Wind | Wind | Wind Onshore | 1 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | 60 | 0.99 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 0.3402 | 1500 | #N/A | #N/A | 34.02 | #N/A
Shed1h | DSM shed | Generator | Shed | Shed | Shed |  |  |  | 1 | nonCHP | DSM | DSM | DSM | DSM | 0 | 0 |  | DSM | DSM | DSM | DSM | DSM | DSM | Other | DSM | DSM | DSM | DSM | DSM | No | DSM | None | None | None | None | DSM | Shed1h | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shed4h | DSM shed | Generator | Shed | Shed | Shed |  |  |  | 1 | nonCHP | DSM | DSM | DSM | DSM | 0 | 0 |  | DSM | DSM | DSM | DSM | DSM | DSM | Other | DSM | DSM | DSM | DSM | DSM | No | DSM | None | None | None | None | DSM | Shed4h | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shed10h | DSM shed | Generator | Shed | Shed | Shed |  |  |  | 1 | nonCHP | DSM | DSM | DSM | DSM | 0 | 0 |  | DSM | DSM | DSM | DSM | DSM | DSM | Other | DSM | DSM | DSM | DSM | DSM | No | DSM | None | None | None | None | DSM | Shed10h | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift1h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 1h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift3h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 3h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift2h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 2h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift4h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 4h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift5h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 5h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift8h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 8h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift10h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 10h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift12h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 12h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Shift24h | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | 24h | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Al | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | Al | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
EV | DSM shift | Purchaser | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Purchaser | #N/A | #N/A | Purchaser | Purchaser |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Purchaser | Purchaser | Purchaser | Purchaser | #N/A | #N/A | #N/A | #N/A | EV | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
CO2 | Emission | Emission | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Emissions | #N/A | #N/A | Emissions | Emissions |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Emissions | Emissions | Emissions | Emissions | #N/A | #N/A | #N/A | #N/A | CO2 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
NOx | Emission | Emission | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Emissions | #N/A | #N/A | Emissions | Emissions |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Emissions | Emissions | Emissions | Emissions | #N/A | #N/A | #N/A | #N/A | NOx | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
PM | Emission | Emission | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Emissions | #N/A | #N/A | Emissions | Emissions |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Emissions | Emissions | Emissions | Emissions | #N/A | #N/A | #N/A | #N/A | PM | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
SOx | Emission | Emission | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Emissions | #N/A | #N/A | Emissions | Emissions |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Emissions | Emissions | Emissions | Emissions | #N/A | #N/A | #N/A | #N/A | SOx | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Fuel | Fuel | Fuel | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Fuel | #N/A | #N/A | Fuel | Fuel |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Fuel | Fuel | Fuel | Fuel | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Line | Line | Line | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Line | #N/A | #N/A | Line | Line |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Line | Line | Line | Line | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Node | Node | Node | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Node | #N/A | #N/A | Node | Node |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Node | Node | Node | Node | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Region | Region | Region | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Region | #N/A | #N/A | Region | Region |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Region | Region | Region | Region | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Zone | Zone | Zone | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Zone | #N/A | #N/A | Zone | Zone |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Zone | Zone | Zone | Zone | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Area | Area | Area | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Area | #N/A | #N/A | Area | Area |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Area | Area | Area | Area | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Reserve | Reserve | Reserve | Excluded | #N/A | #N/A | #N/A |  |  | #N/A | Reserve | #N/A | #N/A | Reserve | Reserve |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | Reserve | Reserve | Reserve | Reserve | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Variable | Variable | Variable | Excluded | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
Note on BK1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Uses DEA, unless data is missing. Thereafter, NREL ATB Reply: Should update each project
Note on BL1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Uses DEA, unless data is missing. Thereafter, NREL ATB Reply: Should update each project
Note on BW1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not currently used. CAPEX data instead is captured per technology in the model. Could be used directly here (with DEA data, for different years) Reply: Should update each project

## MaxCapacity
Combining main data sources |  | Original (Multi-source)
DEA_NAME | NAME_original | Max Cap | SOURCE
Coal Subcritical | Coal lignite | 800 | based on coal supercritical
Coal Subcritical | Coal subcritical | 800 | based on coal supercritical
Coal Supercritical | Coal supercritical | 800 | NREL india greening the grid
Coal Ultra supercritical | Coal ultrasupercritical | 800 | based on coal supercritical
IGCC | IGCC | 800 | based on coal supercritical
CCGT | CCGT | 600 | NREL india greening the grid
CCGT | Steam turbine (Gas/Oil) | 600 | DEA
SCGT | OCGT | 400 | NREL india greening the grid
#N/A | Fuel cell | 1 | Assumed
Nuclear | Nuclear | 1000 | Assumed
Mini-micro hydro power plant | Hydro RoR | 5 | DEA
Medium-small hydro power plant | Hydro RoRpondage | 50 | DEA
Large hydro power plant | Hydro Reservoir | 150 | DEA
Biomass power plant (small) | Solid biomass | 25 | DEA
Biogas power plant (small) | Biogas | 1 | DEA
Geothermal - large | Geothermal | 55 | DEA
Wind Onshore | Wind onshore | 1 | Assumed
Wind Offshore | Wind offshore | 1 | Assumed
Ground-mounted PV | Solar PV Utility | 1 | Assumed
Rooftop PV | Solar PV Buildings | 1 | Assumed
#N/A | Solar CSP | 100 | Assumed
Tidal Stream | Ocean energy | 1 | Assumed
Hydro pumped storage | Hydro PSH | 250 | DEA
Batteries | Battery | 1 | Assumed
#N/A | CHP Other | 20 | Assumed for completeness
#N/A | CHP Coal | 100 | Assumed for completeness
#N/A | CHP Gas | 20 | Assumed for completeness
#N/A | CHP Geothermal | 50 | Assumed for completeness
#N/A | CHP Nuclear | 500 | Assumed for completeness
#N/A | CHP Oil | 5 | Assumed for completeness
#N/A | CHP OtherSources | 5 | Assumed for completeness
#N/A | CHP Solar | 100 | Assumed for completeness
techs with 1 use the max cap to define number of units (1) and then set the capacity based on no of units column in Capacity sheet - workaround to allow them to be handled easily in the worksheet and avoid needing to set different max caps for the same technology in different regions

## MinStableLevel
|  | SOURCE: Upper range of APPFC or Agora | Source: DEA Indonesia, APPFC mean
DEA_NAME | NAME | MSL existing/inflex | MSL (based on DEA or average of APPFC) | MSL flex
Coal Subcritical | Coal lignite | 60 | 30 | 30
Coal Subcritical | Coal subcritical | 60 | 30 | 10
Coal Supercritical | Coal supercritical | 50 | 25 | 20
Coal Ultra supercritical | Coal ultrasupercritical | 50 | 30 | 20 | SOURCE: Gujarat/India CEA feedback | SOURCE: APPFC report ranges (orig, to verify where the values are from) | SOURCE: PST 2018, APPFC report ranges |  | SOURCE: Agora, common plants | https://www.agora-energiewende.de/fileadmin/Projekte/2017/Flexibility_in_thermal_plants/115_flexibility-report-WEB.pdf |  | Source: DEA Indonesia | MSL (%) - 2020 | MSL (%) - 2030 | *Properties for new builds
IGCC | IGCC | 50 | 50 | 20 | MSL% | MSL flex | MSL (%) - min | MSL (%) - max | MSL (%) - lower | MSL (%) - upper | <<Choose the higher of the MSL from Agora/APPFC | Geothermal - large | #N/A | #N/A
#N/A | CHP | 50 | 35 | 20 | 75 | 45 | #N/A | #N/A | 50 | 60 |  | Geothermal - small | #N/A | #N/A
CCGT | CCGT | 50 | 45 | 15 | 55 | 45 | 10 | 60 | 25 | 40 |  | Large hydro power plant | #N/A | #N/A
CCGT | Steam turbine (Gas/Oil) | 50 | 45 | 20 | 55 | 45 | 20 | 50 | 25 | 40 |  | Medium-small hydro power plant | #N/A | #N/A
SCGT | OCGT | 50 | 20 | 10 | 55 | 45 | 20 | 50 | 25 | 40 |  | Mini-micro hydro power plant | #N/A | #N/A
#N/A | Fuel cell | #N/A | #N/A | #N/A | 55 | 50 | 20 | 50 | 25 | 40 |  | Hydro pumped storage | #N/A | #N/A
Nuclear | Nuclear | 50 | 40 | 30 | #N/A | #N/A | 20 | 50 | 25 | 40 |  | Ground-mounted PV | #N/A | #N/A
Mini-micro hydro power plant | Hydro RoR | 0 | 0 | 0 | 40 | 40 | 15 | 40 | 40 | 50 |  | Rooftop PV | #N/A | #N/A
Medium-small hydro power plant | Hydro RoRpondage | 0 | 0 | 0 | 40 | 30 | 20 | 50 | 40 | 50 |  | Industrial PV | #N/A | #N/A
Large hydro power plant | Hydro Reservoir | 0 | 0 | 0 | 35 | 35 | 10 | 50 | 20 | 50 |  | Floating PV | #N/A | #N/A
Biomass power plant (small) | Solid biomass | 30 | 30 | 25 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | Wind Onshore | #N/A | #N/A
Biogas power plant (small) | Biogas | 20 | 15 | 10 | 70 | 50 | 30 | 50 | #N/A | #N/A |  | Small wind onshore | #N/A | #N/A
Geothermal - large | Geothermal | #N/A | #N/A | #N/A | 6 | 6 | 0 | 0 | #N/A | #N/A |  | Wind Offshore | #N/A | #N/A
Wind Onshore | Wind onshore | #N/A | #N/A | #N/A | 6 | 6 | 0 | 0 | #N/A | #N/A |  | Tidal Impoundment | #N/A | #N/A
Wind Offshore | Wind offshore | #N/A | #N/A | #N/A | 6 | 6 | 0 | 0 | #N/A | #N/A |  | Tidal Stream | #N/A | #N/A
Ground-mounted PV | Solar PV Utility | #N/A | #N/A | #N/A | #N/A | #N/A | 25 | 30 | #N/A | #N/A |  | Coal Subcritical | 30 | 30
Rooftop PV | Solar PV Buildings | #N/A | #N/A | #N/A | #N/A | #N/A | 10 | 20 | #N/A | #N/A |  | Coal Supercritical | 25 | 25
#N/A | Solar CSP | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | Coal Ultra supercritical | 30 | 30
Tidal Stream | Ocean energy | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | IGCC | 50 | 50
Hydro pumped storage | Hydro PSH | 33 | 33 | 0 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | CCGT | 45 | 45
Diesel power plant | #N/A | 40 | 35 | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | SCGT | 20 | 20
| **HydroPSH had 33% for existing, but I have lost the reference |  |  |  | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | CCS - Supercritical coal | 30 | 30
[5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | CCS - CCGT | 45 | 45
[5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | CCS - IGCC | 50 | 50
[12 empty] | Biomass power plant (small) | 30 | 30
[5 empty] | #N/A | #N/A | 30 | 40 | #N/A | #N/A |  | Batteries | #N/A | #N/A

## RampRates
Combining main data sources |  | SOURCE: APPFC | Using a single rate for up and down only for now as data is symmetric | https://www.agora-energiewende.de/fileadmin/Projekte/2017/Flexibility_in_thermal_plants/115_flexibility-report-WEB.pdf |  | Source: DEA Indonesia | Flex/inflex ramp rates based on APPFC/DEA/Agora
| UNITS | %/min | MW/min | Agora current |  | %/min | %/min | %/min
DEA_NAME | NAME | Ramp up/down | Ramp up/down | Ramp - lower range | Ramp - upper range | Ramp up/down | Existing | New/Retrofit | Inflex (lower range of Agora)
Coal Subcritical | Coal lignite | 4 | 0.066667 | 1 | 2 | 3.5 | 1.5 | 3.5 | 1 | 1
Coal Subcritical | Coal subcritical | 4 | 0.066667 | 1.5 | 4 | 3.5 | 2.75 | 3.5 | 1.5
Coal Supercritical | Coal supercritical | 4 | 0.066667 | 1.5 | 4 | 4 | 2.75 | 4 | 1.5
Coal Ultra supercritical | Coal ultrasupercritical | 4 | 0.066667 | 1.5 | 4 | 5 | 2.75 | 5 | 1.5
IGCC | IGCC | 4 | 0.066667 | 1.5 | 4 | 3 | 2.75 | 3 | 1.5 |  |  | SOURCE: APPFC
CCGT | CCGT | 6 | 0.1 | 2 | 4 | 20 | 3 | 20 | 2 |  |  | UNITS | %/min | %/min | MW/min | MW/min
CCGT | Steam turbine (Gas/Oil) | 3.5 | 0.058333 | 2 | 4 | 20 | 3 | 20 | 2 |  |  | NAME | Ramp up | Ramp down | Ramp up | Ramp down
SCGT | OCGT | 11.5 | 0.19167 | 8 | 12 | 20 | 10 | 20 | 8 | ***based on new source! | https://www.sciencedirect.com/science/article/pii/S0306261918303180 | Coal lignite | 4 | 4 | 0.066667 | 0.066667
Nuclear | Nuclear | 3 | 0.05 | 0.5 | 0.5 | #N/A | 0.5 | 3 | 0.5 |  |  | Coal subcritical | 4 | 4 | 0.066667 | 0.066667
Mini-micro hydro power plant | Hydro RoR | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 |  |  | Coal supercritical | 4 | 4 | 0.066667 | 0.066667
Medium-small hydro power plant | Hydro RoRpondage | #N/A | #N/A |  |  | 50 | 50 | 50 | 0 |  |  | Coal ultrasupercritical | 4 | 4 | 0.066667 | 0.066667
Large hydro power plant | Hydro Reservoir | #N/A | #N/A |  |  | 50 | 50 | 50 | 0 |  |  | IGCC | 4 | 4 | 0.066667 | 0.066667
Hydro pumped storage | Hydro PSH | #N/A | #N/A |  |  | 50 | 50 | 50 | 0 |  |  | CCGT | 6 | 6 | 0.1 | 0.1
Geothermal - large | #N/A | #N/A | #N/A |  |  | 3 | 3 | 3 | 0
Geothermal - small | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 |  |  | Steam turbine (Gas/Oil) | 3.5 | 3.5 | 0.058333 | 0.058333
Tidal Impoundment | #N/A | #N/A | #N/A |  |  | 50 | 50 | 50 | 0 |  |  | OCGT | 11.5 | 11.5 | 0.19167 | 0.19167
CCS - Supercritical coal | #N/A | #N/A | #N/A |  |  | 4 | 4 | 4 | 0 |  |  | Nuclear | 3 | 3 | 0.05 | 0.05
CCS - CCGT | #N/A | #N/A | #N/A |  |  | 20 | 20 | 20 | 0 |  |  | Hydro RoR | #N/A | #N/A | #N/A | #N/A
CCS - IGCC | #N/A | #N/A | #N/A |  |  | 3 | 3 | 3 | 0 |  |  | Hydro RoRpondage | #N/A | #N/A | #N/A | #N/A
Biomass power plant (small) | #N/A | #N/A | #N/A |  |  | 10 | 10 | 10 | 0 |  |  | Hydro Reservoir | #N/A | #N/A | #N/A | #N/A
Biogas power plant (small) | #N/A | #N/A | #N/A |  |  | 20 | 20 | 20 | 0 |  |  | Hydro PSH | #N/A | #N/A | #N/A | #N/A
MSW incineration | #N/A | #N/A | #N/A |  |  | 10 | 10 | 10 | 0
Landfill | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0
Diesel power plant | #N/A | #N/A | #N/A |  |  | 25 | 25 | 25 | 0 |  |  | Manually made zero/- = #N/A | 2020 | 2030
Batteries | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | 0 |  |  | Source: DEA Indonesia | Ramp (% per min) | Ramp (% per min)
Solid biomass | Solid biomass | 4 | 0.066667 | 1.5 | 4 | 3.5 | 2.75 | 3.5 | 1.5 | **based on coal |  | Geothermal - large | 3 | 3
Biogas | Biogas | 11.5 | 0.19167 | 8 | 12 | 20 | 10 | 20 | 8 | based on gas |  | Geothermal - small | #N/A | #N/A
Geothermal | Geothermal | 4 | 0.066667 | 1.5 | 4 | 3.5 | 2.75 | 3.5 | 1.5 | **based on coal |  | Large hydro power plant | 50 | 50
[12 empty] | Medium-small hydro power plant | 50 | 50
[12 empty] | Mini-micro hydro power plant | #N/A | #N/A
[12 empty] | Hydro pumped storage | 50 | 50
[12 empty] | Ground-mounted PV | #N/A | #N/A
[12 empty] | Rooftop PV | #N/A | #N/A
[12 empty] | Industrial PV | #N/A | #N/A
[12 empty] | Floating PV | #N/A | #N/A
[12 empty] | Wind Onshore | #N/A | #N/A
[12 empty] | Small wind onshore | #N/A | #N/A
[12 empty] | Wind Offshore | #N/A | #N/A
[12 empty] | Tidal Impoundment | 50 | 50
[12 empty] | Tidal Stream | #N/A | #N/A
[12 empty] | Coal Subcritical | 3.5 | 3.5
[12 empty] | Coal Supercritical | 4 | 4
[12 empty] | Coal Ultra supercritical | 5 | 5
[12 empty] | IGCC | 3 | 3
[12 empty] | CCGT | 20 | 20
[12 empty] | SCGT | 20 | 20
[12 empty] | CCS - Supercritical coal | 4 | 4
[12 empty] | CCS - CCGT | 20 | 20
[12 empty] | CCS - IGCC | 3 | 3
[12 empty] | Biomass power plant (small) | 10 | 10
[12 empty] | Biogas power plant (small) | 20 | 20
[12 empty] | MSW incineration | 10 | 10
[12 empty] | Landfill | #N/A | #N/A
[12 empty] | Diesel power plant | 25 | 25
[12 empty] | Batteries | #N/A | #N/A
Note on E12: HART Craig, IEA/EMS/RISE: From https://www.sciencedirect.com/science/article/pii/S0306261918303180 which contains specific info on nuclear

## StartUpTimes
SOURCE: Assumed
UNITS | hours
NAME | Run up factor
Coal lignite | 0.9 | Start-up times as below are not modelled as this includes times that would be included in the notice period for starting the generators (as reflected in the scheduling interval of the generators)
Coal subcritical | 0.9 | SOURCE: APPFC
Coal supercritical | 0.9 | UNITS | hours | hours | hours |  | From Thailand - factor used to calculate run up relative to ramp rate
Coal ultrasupercritical | 0.9 | NAME | hot | warm | cold |  | Class | RunUpFactor
IGCC | 0.9 | Gas CCGT | 0.4 | 1 | 1.75 |  | HYDRO | NA
CCGT | 0.9 | Gas OCGT | 0.2 | 0.2 | 0.2 |  | COAL | 0.9
Steam turbine (Gas/Oil) | 0.9 | Steam turbine (Gas/Oil) | 2.5 | 2.5 | 2.5 |  | CCGT | 0.9
OCGT | 0.9 | Coal supercritical | 2 | 4.5 | 6.5 |  | OCGT | 0.9
Nuclear | 0.9 | Nuclear Light Water | 1 | 2 | 48 |  | Thermal_gas | 0.9
Solid biomass | 0.9 | Solid biomass | 1.5 | 3 | 4 |  | DIESEL | 1
Biogas | 0.9 | [5 empty] | HYDRO_import | NA
Geothermal | 0.9 | [5 empty] | FUEL OIL | 0.9
|  | UNITS | %/min | %/min | MW/min | MW/min | NUCLEAR | 0.9
|  | NAME | Ramp up | Ramp down | Ramp up | Ramp down
|  | Coal lignite | 4 | 4 | 0.066667 | 0.066667
|  | Coal subcritical | 4 | 4 | 0.066667 | 0.066667
|  | Coal supercritical | 4 | 4 | 0.066667 | 0.066667
|  | Coal ultrasupercritical | 4 | 4 | 0.066667 | 0.066667
|  | IGCC | 4 | 4 | 0.066667 | 0.066667
|  | CCGT | 6 | 6 | 0.1 | 0.1
|  | Steam turbine (Gas/Oil) | 3.5 | 3.5 | 0.058333 | 0.058333
|  | OCGT | 11.5 | 11.5 | 0.19167 | 0.19167
|  | Nuclear | 3 | 3 | 0.05 | 0.05
|  | Source: DEA Indonesia | Warm start-up time (hours) | Cold start-up time (hours)
|  | Large hydro power plant | 0.1 | 0.1
|  | Medium-small hydro power plant | 0.1 | 0.1
|  | Hydro pumped storage | 0.1 | 0.1
|  | Tidal Impoundment | 0.1 | 0.1
|  | Coal Subcritical | 3 | 8
|  | Coal Supercritical | 4 | 12
|  | Coal Ultra supercritical | 4 | 12
|  | IGCC | 6 | 15-80
|  | CCGT | 2 | 4
|  | SCGT | 0.25 | 0.5
|  | CCS - Supercritical coal | 4 | 12
|  | CCS - CCGT | 2 | 4
|  | CCS - IGCC | 6 | 15-80
|  | Biomass power plant (small) | 0.5 | 10
|  | Biogas power plant (small) | 0 | 0
|  | MSW incineration | 0.5 | 2
|  | Diesel power plant | 0.05 | 0.3

## StartCosts
| Source: Power Plant Cycling Costs |  | MEDIANS OF LOWER BOUND COSTS
|  | USD/MW | https://www.nrel.gov/docs/fy12osti/55433.pdf |  | ACIL ALLEN
DEA_Name | NAME | Start Cost Hot | Start Cost Warm | Start Cost Cold | CoolingTime1 | CoolingTime2 | CoolingTime3 | Start-up costs single ($/MWe/start-up) - DEA
Coal Subcritical | Coal lignite | 54 | 64 | 104 | 2 | 4 | 24 | 110 |  |  |  | OLD values from ETP cooling model
Coal Subcritical | Coal subcritical | 54 | 64 | 104 | 2 | 4 | 24 | 110 |  |  |  | Source: Power Plant Cycling Costs |  | MEDIANS OF LOWER BOUND COSTS |  |  | SOURCE: ACIL ALLEN
Coal Supercritical | Coal supercritical | 54 | 64 | 104 | 2 | 4 | 24 | 50 |  |  |  |  | USD/MW |  |  |  | hours | hours | hours
Coal Ultra supercritical | Coal ultrasupercritical | 54 | 64 | 104 | 2 | 4 | 24 | 50 |  |  |  | NAME | Start Cost Hot | Start Cost Warm | Start Cost Cold |  | CoolingTime1 | CoolingTime2 | CoolingTime3 | CT1 incr | CT2 incr | CT3 incr
IGCC | IGCC | 54 | 64 | 104 | 1 | 3 | 15 | 100 |  |  | CCGT | Gas CCGT | 35 | 55 | 79 |  | 1 | 3 | 15 | 1 | 2 | 12
CCGT | CCGT | 35 | 55 | 79 | 1 | 3 | 15 | 80 |  |  | OCGT | Gas OCGT | 32 | 126 | 103 |  | 1 | 1 | 1 | 1 | 0 | 0
CCGT | Steam turbine (Gas/Oil) | 36 | 58 | 75 | 2 | 4 | 24 | 80 |  |  | Steam turbine (Gas/Oil) | Steam turbine (Gas/Oil) | 36 | 58 | 75 |  | 2 | 4 | 24 | 2 | 2 | 20 | **
SCGT | OCGT | 32 | 126 | 103 | 1 | 1 | 1 | 24 |  |  | Coal supercritical | Coal supercritical | 54 | 64 | 104 |  | 2 | 4 | 24 | 2 | 2 | 20
Nuclear | Nuclear | 162 | 192 | 312 | 2 | 4 | 24 | 330 | ** need to fix - currently 3* coal |  | Nuclear | Nuclear Light Water | 162 | 192 | 312 | ** need to fix - currently 3* coal | 2 | 4 | 24 | 2 | 2 | 20 | **
CCS - Supercritical coal | CCS - Supercritical coal | 54 | 64 | 104 | 2 | 4 | 24 | 50 |  |  | Solid biomass | Solid biomass | 40 | 60 | 90 | ** gas/coal av | 2 | 4 | 24 | 2 | 2 | 20 | **
CCS - CCGT | CCS - CCGT | 35 | 55 | 79 | 1 | 3 | 15 | 80 |  | Assumed | Coal lignite | [5 empty] | 2 | 4 | 24
CCS - IGCC | CCS - IGCC | 54 | 64 | 104 | 1 | 3 | 15 | 100 |  | Assumed | Coal subcritical | [5 empty] | 2 | 4 | 24
Solid biomass | Solid biomass | 54 | 64 | 104 | 2 | 4 | 24 | 110 | *** based on Coal Subcritical | Assumed | Coal supercritical | [5 empty] | 2 | 4 | 24
Biogas | Biogas | 32 | 126 | 103 | 1 | 1 | 1 | 24 | *** based on OCGT | Assumed | Coal ultrasupercritical | [5 empty] | 2 | 4 | 24
Geothermal | Geothermal | 54 | 64 | 104 | 2 | 4 | 24 | 110 | *** based on Coal Subcritical | Assumed | Geothermal | [5 empty] | 2 | 4 | 24
[10 empty] | Assumed | Biogas | [5 empty] | 1 | 1 | 1
[11 empty] | IGCC | [5 empty] | 1 | 3 | 15
[11 empty] | CCS - Supercritical coal | [5 empty] | 2 | 4 | 24
[11 empty] | CCS - CCGT | [5 empty] | 1 | 3 | 15
[11 empty] | CCS - IGCC | [5 empty] | 1 | 3 | 15
** based on coal
[12 empty] | Source: DEA Indonesia | Start-up costs ($/MWe/start-up) |  | *Properties for new builds
[12 empty] | Coal Subcritical | 110
[12 empty] | Coal Supercritical | 50
[12 empty] | Coal Ultra supercritical | 50
[12 empty] | IGCC | 100
[12 empty] | CCGT | 80
Note on E3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: Power Plant Cycling Costs Reply: https://www.nrel.gov/docs/fy12osti/55433.pdf
Note on J3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Source: DEA Indonesia

## MinUpAndDown
|  | … NEW | values from ERAA can be put here!!
UNITS | hours | hours | … NEW | values from ERAA can be put here!!
NAME | Min up time | Min down time | Min up time flex | Min down time flex
Coal lignite | 8 | 8 | #N/A | #N/A
Coal subcritical | 8 | 8 | #N/A | #N/A
Coal supercritical | 8 | 8 | #N/A | #N/A |  | From cooling | SOURCE: ACIL ALLEN EXISTING PLANT
Coal ultrasupercritical | 8 | 8 | #N/A | #N/A
IGCC | 8 | 8 | #N/A | #N/A |  |  | UNITS | hours | hours
CCGT | 4 | 4 | #N/A | #N/A |  |  | NAME | Min up time | Min down time
OCGT | 1 | 1 | #N/A | #N/A |  |  | Gas CCGT | 4 | 4
Nuclear | 120 | 120 | #N/A | #N/A | ** made up |  | Gas OCGT | 1 | 1
Solid biomass | 4 | 4 | #N/A | #N/A | based on coal |  | Steam turbine (Gas/Oil) | 8 | 8
Biogas | 8 | 8 | #N/A | #N/A | based on OCGT |  | Coal supercritical | 8 | 8
Geothermal | 4 | 4 | #N/A | #N/A | based on coal |  | Nuclear Light Water | 20 | 20 | ** made up
Steam turbine (Gas/Oil) | 8 | 8 | #N/A | #N/A |  |  | Solid biomass | 8 | 8 | based on coal
[7 empty] | Biogas | 1 | 1 | based on OCGT
[7 empty] | Geothermal | 8 | 8 | based on coal
Note on D3: HART Craig, IEA/EMS/RISE: no flex values here. If we want this, must be sourced from another project (e.g. China?)
Note on N6: HART Craig, IEA/EMS/RISE: to update with ERAA inputs

## LHVs
This should be updated for each project as best possible. | SOURCE |  |  | WEO 2017 for 2040 (China) | 2040 | 2030 DEA
Equivalent of the Efficiency table from model_setup (legacy version) |  |  |  | LHV % | GJ/MWh | GJ/MWh
DEA NAME | Plant type | WEO_Tech | PLEXOS technology (NEW) | 2040 efficiency
#REF! | [Coal Subcritical 1] | Coal Subcritical 1 |  | 0.31639 | 11.3784 | #REF! |  |  | 2020 |  | 2030
#REF! | [Coal Subcritical 2] | Coal Subcritical 2 |  | 0.34205 | 10.5248 | #REF! |  | Source: DEA Indonesia | LHV (%) | GJ/MWh | LHV (%) | GJ/MWh | *Properties for new builds
#REF! | [Coal Subcritical 3] | Coal Subcritical 3 |  | 0.32353 | 11.1273 | #REF! |  | Geothermal - large | 15 | 24 | 15 | 24
#REF! | [Coal Subcritical 4] | Coal Subcritical 4 |  | 0.3345 | 10.7623 | #REF! |  | Geothermal - small | 10 | 36 | 10 | 36
#REF! | [Coal Subcritical 5] | Coal Subcritical 5 |  | 0.35254 | 10.2116 | #REF! |  | Large hydro power plant | 95 | 3.7895 | 95 | 3.7895
#REF! | [Coal Supercritical 1] | Coal Supercritical 1 |  | 0.26 | 13.8462 | #REF! |  | Medium-small hydro power plant | 95 | 3.7895 | 95 | 3.7895
#REF! | [Coal Supercritical 2] | Coal Supercritical 2 |  | 0.37454 | 9.6118 | #REF! |  | Mini-micro hydro power plant | 80 | 4.5 | 80 | 4.5
#REF! | [Coal Supercritical 3] | Coal Supercritical 3 |  | 0.31 | 11.6129 | #REF! |  | Hydro pumped storage | 80 | 4.5 | 80 | 4.5
#REF! | [Coal Supercritical 4] | Coal Supercritical 4 |  | 0.31 | 11.6129 | #REF! |  | Ground-mounted PV | #N/A | #N/A | #N/A | #N/A
#REF! | [Coal Supercritical 5] | Coal Supercritical 5 |  | 0.3839 | 9.3774 | #REF! |  | Rooftop PV | #N/A | #N/A | #N/A | #N/A
#REF! | [Coal Ultrasupercritical 1] | Coal Ultrasupercritical 1 |  | 0.44 | 8.1818 | #REF! |  | Industrial PV | #N/A | #N/A | #N/A | #N/A
#REF! | [Coal Ultrasupercritical 2] | Coal Ultrasupercritical 2 |  | 0.44 | 8.1818 | #REF! |  | Floating PV | #N/A | #N/A | #N/A | #N/A
#REF! | [Coal Ultrasupercritical 3] | Coal Ultrasupercritical 3 |  | 0.44 | 8.1818 | #REF! |  | Wind Onshore | 100 | 3.6 | 100 | 3.6
#REF! | [Coal Ultrasupercritical 4] | Coal Ultrasupercritical 4 |  | 0.44 | 8.1818 | #REF! |  | Small wind onshore | 100 | 3.6 | 100 | 3.6
#REF! | [Coal Ultrasupercritical 5] | Coal Ultrasupercritical 5 |  | 0.44 | 8.1818 | #REF! |  | Wind Offshore | 100 | 3.6 | 100 | 3.6
#REF! | [Coal IGCC 1] | Coal IGCC 1 |  | 0.43 | 8.3721 | #REF! |  | Tidal Impoundment | 90 | 4 | 90 | 4
#REF! | [Coal IGCC 2] | Coal IGCC 2 |  | 0.43 | 8.3721 | #REF! |  | Tidal Stream | 90 | 4 | 90 | 4
#REF! | [Coal IGCC 3] | Coal IGCC 3 |  | 0.41199 | 8.7381 | #REF! |  | Coal Subcritical | 34.33 | 10.4865 | 34.33 | 10.4865
#REF! | [Coal IGCC 4] | Coal IGCC 4 |  | 0.43 | 8.3721 | #REF! |  | Coal Supercritical | 36.67 | 9.8173 | 36.67 | 9.8173
#REF! | [Coal IGCC 5] | Coal IGCC 5 |  | 0.43 | 8.3721 | #REF! |  | Coal Ultra supercritical | 41.5 | 8.6747 | 41.5 | 8.6747
#REF! | [Coal CHP MaxMin] | Coal CHP MaxMin |  | 0 | #N/A | #REF! |  | IGCC | 40 | 9 | 40 | 9
#REF! | [Gas CCGT 1] | Gas CCGT 1 |  | 0.40099 | 8.9778 | #REF! |  | CCGT | 56 | 6.4286 | 56 | 6.4286
#REF! | [Gas CCGT 2] | Gas CCGT 2 |  | 0.42834 | 8.4045 | #REF! |  | SCGT | 32.5 | 11.0769 | 32.5 | 11.0769
#REF! | [Gas CCGT 3] | Gas CCGT 3 |  | 0.45952 | 7.8343 | #REF! |  | CCS - Supercritical coal | -8 | 13.6726 | -8 | 13.6726
#REF! | [Gas CCGT 4] | Gas CCGT 4 |  | 0.31 | 11.6129 | #REF! |  | CCS - CCGT | -8 | 7.5 | -8 | 7.5
#REF! | [Gas CCGT 5] | Gas CCGT 5 |  | 0.31 | 11.6129 | #REF! |  | CCS - IGCC | -8 | 11.25 | -8 | 11.25
#REF! | [Gas Steam 1] | Gas Steam 1 |  | 0.26644 | 13.5115 | #REF! |  | Biomass power plant (small) | 31 | 11.6129 | 31 | 11.6129
#REF! | [Gas Steam 2] | Gas Steam 2 |  | 0.29752 | 12.1 | #REF! |  | Biogas power plant (small) | 34 | 10.5882 | 34 | 10.5882
#REF! | [Gas Steam 3] | Gas Steam 3 |  | 0.33135 | 10.8646 | #REF! |  | MSW incineration | 0.2755 | 1306.7151 | 0.2755 | 1306.7151
#REF! | [Gas Steam 4] | Gas Steam 4 |  | 0.29 | 12.4138 | #REF! |  | Landfill | 34 | 10.5882 | 34 | 10.5882
#REF! | [Gas Steam 5] | Gas Steam 5 |  | 0.29 | 12.4138 | #REF! |  | Diesel power plant | 45 | 8 | 45 | 8
#REF! | [Gas GT 1] | Gas GT 1 |  | 0.25942 | 13.8771 | #REF! |  | Batteries | #N/A | #N/A | 0 | #DIV/0!
#REF! | [Gas GT 2] | Gas GT 2 |  | 0.29155 | 12.3478 | #REF!
#REF! | [Gas GT 3] | Gas GT 3 |  | 0.3178 | 11.3279 | #REF!
#REF! | [Gas GT 4] | Gas GT 4 |  | 0.26 | 13.8462 | #REF!
#REF! | [Gas GT 5] | Gas GT 5 |  | 0.26 | 13.8462 | #REF!
#REF! | [Gas CHP MaxMin] | Gas CHP MaxMin |  | 0 | #N/A | #REF!
#REF! | [Fuel Cell 1] | Fuel Cell 1 |  | 0.3 | 12 | #REF!
#REF! | [Fuel Cell 2] | Fuel Cell 2 |  | 0.3 | 12 | #REF!
#REF! | [Oil Steam 1] | Oil Steam 1 |  | 0.23306 | 15.4467 | #REF!
#REF! | [Oil Steam 2] | Oil Steam 2 |  | 0.25114 | 14.3346 | #REF!
#REF! | [Oil Steam 3] | Oil Steam 3 |  | 0.27994 | 12.8599 | #REF!
#REF! | [Oil Steam 4] | Oil Steam 4 |  | 0.29 | 12.4138 | #REF!
#REF! | [Oil Steam 5] | Oil Steam 5 |  | 0.29 | 12.4138 | #REF!
#REF! | [Oil GT 1] | Oil GT 1 |  | 0.23256 | 15.4799 | #REF!
#REF! | [Oil GT 2] | Oil GT 2 |  | 0.25255 | 14.2546 | #REF!
#REF! | [Oil GT 3] | Oil GT 3 |  | 0.25602 | 14.0614 | #REF!
#REF! | [Oil GT 4] | Oil GT 4 |  | 0.26 | 13.8462 | #REF!
#REF! | [Oil GT 5] | Oil GT 5 |  | 0.26 | 13.8462 | #REF!
#REF! | [Oil CHP MaxMin] | Oil CHP MaxMin |  | 0 | #N/A | #REF!
#REF! | [CCS Oxyfuel 1] | CCS Oxyfuel 1 |  | 0.33 | 10.9091 | #REF!
#REF! | [CCS IGCC 1] | CCS IGCC 1 |  | 0.33 | 10.9091 | #REF!
#REF! | [CCS CCGT 1] | CCS CCGT 1 |  | 0.22 | 16.3636 | #REF!
Nuclear | [Nuclear] | Nuclear |  | 0.33 | 10.9091 | #N/A
#REF! | [NEW Coal Lignite] | NEW Coal Lignite |  | 0.345 | 10.4348 | #REF!
#REF! | [NEW Coal Subcritical] | NEW Coal Subcritical |  | 0.36062 | 9.9828 | #REF!
#REF! | [NEW Coal Supercritical] | NEW Coal Supercritical |  | 0.395 | 9.1139 | #REF!
#REF! | [NEW Coal Ultrasupercritical] | NEW Coal Ultrasupercritical |  | 0.41338 | 8.7087 | #REF!
#REF! | [NEW Coal IGCC] | NEW Coal IGCC |  | 0.452 | 7.9646 | #REF!
#REF! | [NEW Gas CCGT] | NEW Gas CCGT |  | 0.56945 | 6.3219 | #REF!
#REF! | [NEW Gas Steam] | NEW Gas Steam |  | 0.37 | 9.7297 | #REF!
#REF! | [NEW Gas GT] | NEW Gas GT |  | 0.3949 | 9.1162 | #REF!
#REF! | [NEW Fuel Cell] | NEW Fuel Cell |  | 0.3 | 12 | #REF!
#REF! | [NEW Oil Steam] | NEW Oil Steam |  | 0.37 | 9.7297 | #REF!
#REF! | [NEW Oil GT] | NEW Oil GT |  | 0.3835 | 9.3872 | #REF!
#REF! | [NEW CCS Coal] | NEW CCS Coal |  | 0.33 | 10.9091 | #REF!
#REF! | [NEW CCS Coal Oxyfuel] | NEW CCS Coal Oxyfuel |  | 0.33 | 10.9091 | #REF!
#REF! | [NEW CCS Coal IGCC] | NEW CCS Coal IGCC |  | 0.33 | 10.9091 | #REF!
#REF! | [NEW CCS Gas CCGT] | NEW CCS Gas CCGT |  | 0.22 | 16.3636 | #REF!
#REF! | [NEW CCS Coal Retrofit] | NEW CCS Coal Retrofit |  | 0.33 | 10.9091 | #REF!
#REF! | [NEW CCS Coal IGCC Retrofit] | NEW CCS Coal IGCC Retrofit |  | 0.33 | 10.9091 | #REF!
#REF! | [NEW CCS Gas CCGT Retrofit] | NEW CCS Gas CCGT Retrofit |  | 0.22 | 16.3636 | #REF!
#REF! | [NEW Coal CHP MaxMin] | NEW Coal CHP MaxMin |  | 0.79518 | 4.5273 | #REF!
#REF! | [NEW Gas CHP MaxMin] | NEW Gas CHP MaxMin |  | 0.85808 | 4.1954 | #REF!
#REF! | [NEW Oil CHP MaxMin] | NEW Oil CHP MaxMin |  | 0.87477 | 4.1154 | #REF!
#REF! | [NEW CCS Coal CHP MaxMin] | NEW CCS Coal CHP MaxMin |  | 0 | #N/A | #REF!
#REF! | [NEW CCS Gas CCGT CHP MaxMin] | NEW CCS Gas CCGT CHP MaxMin |  | 0 | #N/A | #REF!
#REF! | [NEW CCS Coal CHP MaxMin Retrofit] | NEW CCS Coal CHP MaxMin Retrofit |  | 0 | #N/A | #REF!
#REF! | [NEW CCS Gas CCGT CHP MaxMin Retrofit] | NEW CCS Gas CCGT CHP MaxMin Retrofit |  | 0 | #N/A | #REF!
Nuclear | [NEW Nuclear] | NEW Nuclear |  | 0.33 | 10.9091 | #N/A
#REF! | [Refurbishment Coal Subcritical Lignite] | Refurbishment Coal Subcritical Lignite |  | 0.345 | 10.4348 | #REF!
#REF! | [Refurbishment Coal Supercritical Lignite] | Refurbishment Coal Supercritical Lignite |  | 0.36062 | 9.9828 | #REF!
#REF! | [Refurbishment Coal Subcritical Steam] | Refurbishment Coal Subcritical Steam |  | 0.395 | 9.1139 | #REF!
#REF! | [Refurbishment Coal Supercritical Steam] | Refurbishment Coal Supercritical Steam |  | 0.41338 | 8.7087 | #REF!
#REF! | [Refurbishment Gas CCGT] | Refurbishment Gas CCGT |  | 0.56945 | 6.3219 | #REF!
#REF! | [Refurbishment Gas Steam] | Refurbishment Gas Steam |  | 0.37 | 9.7297 | #REF!
#REF! | [Refurbishment Gas GT] | Refurbishment Gas GT |  | 0.3949 | 9.1162 | #REF!
#REF! | [Refurbishment Oil Steam] | Refurbishment Oil Steam |  | 0.37 | 9.7297 | #REF!
#REF! | [Refurbishment Oil GT] | Refurbishment Oil GT |  | 0.3835 | 9.3872 | #REF!
#REF! | [NEW CHP Coal,CHPmin] | NEW CHP Coal,CHPmin |  | 0.5 | 7.2 | #REF!
#REF! | [NEW CHP Oil,CHPmin] | NEW CHP Oil,CHPmin |  | 0.6 | 6 | #REF!
#REF! | [NEW CHP Gas,CHPmin] | NEW CHP Gas,CHPmin |  | 0.58 | 6.2069 | #REF!
#REF! | [NEW CHP Nuclear,CHPmin] | NEW CHP Nuclear,CHPmin |  | 0.33 | 10.9091 | #REF!
#REF! | [NEW CHP BiomassandWaste,CHPmin] | NEW CHP BiomassandWaste,CHPmin |  | 0.55 | 6.5455 | #REF!
#REF! | [NEW CHP Geothermal,CHPmin] | NEW CHP Geothermal,CHPmin |  | 1 | 3.6 | #REF!
#REF! | [NEW CHP Solar,CHPmin] | NEW CHP Solar,CHPmin |  | 1 | 3.6 | #REF!
#REF! | [NEW CHP OtherSources,CHPmin] | NEW CHP OtherSources,CHPmin |  | 1 | 3.6 | #REF!
#REF! | [NEW CCS CHP Coal,CHPmin] | NEW CCS CHP Coal,CHPmin |  | 0.5 | 7.2 | #REF!
#REF! | [NEW CCS CHP Gas CCGT,CHPmin] | NEW CCS CHP Gas CCGT,CHPmin |  | 0.58 | 6.2069 | #REF!
#REF! | [NEW CCS CHP Coal Retrofit,CHPmin] | NEW CCS CHP Coal Retrofit,CHPmin |  | 0.5 | 7.2 | #REF!
#REF! | [NEW CCS CHP Gas CCGT Retrofit,CHPmin] | NEW CCS CHP Gas CCGT Retrofit,CHPmin |  | 0.58 | 6.2069 | #REF!
#REF! | [CHP Coal,CHPmin] | CHP Coal,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP Oil,CHPmin] | CHP Oil,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP Gas,CHPmin] | CHP Gas,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP Nuclear,CHPmin] | CHP Nuclear,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP BiomassandWaste,CHPmin] | CHP BiomassandWaste,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP Geothermal,CHPmin] | CHP Geothermal,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP Solar,CHPmin] | CHP Solar,CHPmin |  | 0 | #N/A | #REF!
#REF! | [CHP OtherSources,CHPmin] | CHP OtherSources,CHPmin |  | 0 | #N/A | #REF!
#REF! | [Biomass Power Plant] | Biomass Power Plant |  | 0.36062 | 9.9828 | #REF! | *** No HRs provided. Based on gas and coal plants (see formules)
#REF! | [Biogases] | Biogases |  | 0.3949 | 9.1162 | #REF!
#REF! | [Biomass Cofiring] | Biomass Cofiring |  | 0.32353 | 11.1273 | #REF!
#REF! | [Biomass IGCC with CCS] | Biomass IGCC with CCS |  | 0.33 | 10.9091 | #REF!
#REF! | [Waste to Energy] | Waste to Energy |  | 0.36062 | 9.9828 | #REF!
#REF! | [CHP Coal] | CHP Coal |  | 0.35254 | 10.2116 | #REF!
#REF! | [CHP Gas] | CHP Gas |  | 0.3178 | 11.3279 | #REF!
#REF! | [CHP BiomassandWaste] | CHP BiomassandWaste |  | 0.36062 | 9.9828 | #REF!
#REF! | [CHP Oil] | CHP Oil |  | 0.27994 | 12.8599 | #REF!
#REF! | [Nuclear] | Nuclear |  | 0.33 | 10.9091 | #REF!

## O&M
Should update every project |  | Source: DEA Indonesia, 2025 |  | Source: DEA Indonesia, 2030 |  | SOURCE: NREL ATB
DEA_Name | NREL_Name | Variable O&M ($/MWh) | FO&M ($ /kW) | Variable O&M ($/MWh) | FO&M ($ /kW) | VO&M | FO&M |  |  |  | SOURCE: NREL ATB | https://data.nrel.gov/submissions/89 |  |  | SOURCE: NREL ATB | https://data.nrel.gov/submissions/89
Geothermal - large | Geothermal | 0.25 | 50 | 0.25 | 50 | 0 | 131 |  |  |  | NAME | VO&M | FO&M |  | NAME | VO&M | FO&M
Geothermal - small | #N/A | 0.37 | 65 | 0.37 | 65 | #N/A | #N/A |  |  |  | Lignite | 6.25 | 42.802 | *** scaled according to ACIL ALLEN ratio | Lignite | 6.25 | 42.802 | *** scaled according to ACIL ALLEN ratio
Large hydro power plant | Hydro | 0.65 | 37.7 | 0.65 | 37.7 | 0 | 78 |  |  |  | Coal | 5 | 33 |  |  | 5 | 33
Medium-small hydro power plant | #N/A | 0.5 | 41.9 | 0.5 | 41.9 | #N/A | #N/A | SOURCE: ACIL ALLEN, SA Fuel & Technology Cost report |  |  | Coal CCS | 7 | 69 |  | Coal CCS | 7 | 69
Mini-micro hydro power plant | #N/A | 0.5 | 53 | 0.5 | 53 | #N/A | #N/A |  |  |  | IGCC | 8 | 54 |  | IGCC | 8 | 54
Hydro pumped storage | PSH | 1.325 | 8 | 1.325 | 8 | 3.6542 | 3.6542 |  |  |  | IGCC CCS | 10 | 90 | **derived from above | IGCC CCS | 10 | 90 | **derived from above
Ground-mounted PV | Solar PV Utility | 0 | 14.4 | 0 | 14.4 | 0 | 14 | Biomass | 125000 | 8 | CCGT | 3 | 10 |  | CCGT | 3 | 10
Rooftop PV | Solar PV Buildings | 0 | 14.4 | 0 | 14.4 | 0 | 18 | CCGT - With CCS | 17000 | 12 | Steam turbine (Gas/Oil) | 7 | 12 |  | Steam turbine (Gas/Oil) | 7 | 12
Industrial PV | #N/A | 0 | 14.4 | 0 | 14.4 | #N/A | #N/A | CCGT - Without CCS | 10000 | 7 | OCGT | 7 | 12 |  | OCGT | 7 | 12
Floating PV | #N/A | 0 | 16.2 | 0 | 16.2 | #N/A | #N/A | Integrated Solar Combined Cycle (ISCS) | 15000 | 10 | CCGT CCS | 7 | 33 |  | CCGT CCS | 7 | 33
Wind Onshore | Wind Onshore | 0 | 60 | 0 | 60 | 0 | 51 | Large Scale Battery Storage | 30000 | 6 | PSH | 3.6542 | 3.6542 | *Used ACIL Allen | PSH | 3.6542 | 3.6542 | *Used ACIL Allen
Small wind onshore | #N/A | 0 | 73.2 | 0 | 73.2 | #N/A | #N/A | OCGT - Without CCS | 4000 | 10 | Hydro | 0 | 78 |  | Hydro | 0 | 78
Wind Offshore | Wind Offshore | 5.5 | 72.6 | 5.5 | 72.6 | 0 | 132.38 | Pumped Hydro Storage | 5000 | 5 | Nuclear | 2 | 99 |  | Nuclear | 2 | 99
Tidal Impoundment | #N/A | 0 | 70.8 | 0 | 70.8 | #N/A | #N/A | Solar PV SAT | 30000 | 0 | Biomass | 5 | 110 |  | Biomass | 5 | 110
Tidal Stream | #N/A | 11.7257 | 283 | 11.7257 | 283 | #N/A | #N/A | Solar PV DAT | 39000 | 0 | Solar CSP | 4.1 | 67 |  | Solar CSP | 4.1 | 67
Coal Subcritical | Coal | 0.125 | 45.3 | 0.125 | 45.3 | 5 | 33 | Solar PV FFP | 25000 | 0 | Solar PV Utility | 0 | 14 |  | Solar PV Utility | 0 | 14
Coal Supercritical | #N/A | 0.12 | 41.2 | 0.12 | 41.2 | #N/A | #N/A | Solar Thermal CLF | 64000 | 15.2 | Solar PV Buildings | 0 | 18 |  | Solar PV Buildings | 0 | 18
Coal Ultra supercritical | #N/A | 0.11 | 56.6 | 0.11 | 56.6 | #N/A | #N/A | Solar Thermal CR WS | 72000 | 5.7 | Wind Onshore | 0 | 51 |  | Wind Onshore | 0 | 51
IGCC | IGCC | 12 | 60 | 12 | 60 | 8 | 54 | Solar Thermal PT WS | 73000 | 11.4 | Wind Offshore | 0 | 132.38 |  | Wind Offshore | 0 | 132.38
CCGT | IGCC CCS | 2.3 | 23.5 | 2.3 | 23.5 | 10 | 90 | Supercritical PC - Black coal with CCS | 73200 | 9 | Battery | 2.793 | 9.177 |  | Battery | 0 | 9.177
SCGT | OCGT | 0 | 23.2 | 0 | 23.2 | 7 | 12 | Supercritical PC - Black coal without CCS | 50500 | 4 | Geothermal | 0 | 131 |  | Geothermal | 0 | 131
CCS - Supercritical coal | Coal CCS | 3.1 | 41.8 | 3.1 | 41.8 | 7 | 69 | Supercritical PC - Brown coal with CCS | 96500 | 11
CCS - CCGT | CCGT CCS | 1.2 | 9 | 1.2 | 9 | 7 | 33 | Supercritical PC - Brown coal without CCS | 65500 | 5
CCS - IGCC | IGCC CCS | 5.3 | 8.9 | 5.3 | 8.9 | 10 | 90 | Wind - (100 MW) | 45000 | 15 | Source: DEA Indonesia | Variable O&M ($/MWh) | Fixed O&M ($/MWe/year)
Biomass power plant (small) | Biomass | 3.043 | 47.6 | 3.043 | 47.6 | 5 | 110 | Wave/Ocean | 40000 | 20 | Geothermal - large | 0.25 | 50000
Biogas power plant (small) | #N/A | 0.11 | 97 | 0.11 | 97 | #N/A | #N/A |  |  |  | Geothermal - small | 0.37 | 65000
MSW incineration | #N/A | 24.1437 | 243.7 | 24.1437 | 243.7 | #N/A | #N/A |  |  |  | Large hydro power plant | 0.65 | 37700
Landfill | #N/A | 13.5 | 125 | 13.5 | 125 | #N/A | #N/A |  |  |  | Medium-small hydro power plant | 0.5 | 41900
Diesel power plant | #N/A | 6.4 | 8 | 6.4 | 8 | #N/A | #N/A |  |  |  | Mini-micro hydro power plant | 0.5 | 53000
Batteries | Battery | 0 | 0 | 0 | 0 | 2.793 | 9.177 |  |  |  | Hydro pumped storage | 1.325 | 8000
Nuclear | Nuclear | #N/A | #N/A | #N/A | #N/A | 2 | 99 |  |  |  | Ground-mounted PV | 0 | 14400
#N/A | Steam turbine (Gas/Oil) | #N/A | #N/A | #N/A | #N/A | 7 | 12 |  |  |  | Rooftop PV | 0 | 14400
#N/A | Solar CSP | #N/A | #N/A | #N/A | #N/A | 4.1 | 67 |  |  |  | Industrial PV | 0 | 14400
[11 empty] | Floating PV | 0 | 16200
[11 empty] | Wind Onshore | 0 | 60000
[11 empty] | Small wind onshore | 0 | 73200
[11 empty] | Wind Offshore | 5.5 | 72600
[11 empty] | Tidal Impoundment | 0 | 70800
[11 empty] | Tidal Stream | 11.7257 | 283000
[11 empty] | Coal Subcritical | 0.125 | 45300
[11 empty] | Coal Supercritical | 0.12 | 41200
[11 empty] | Coal Ultra supercritical | 0.11 | 56600
[11 empty] | IGCC | 12 | 60000
[11 empty] | CCGT | 2.3 | 23500
[11 empty] | SCGT | 0 | 23200
[11 empty] | CCS - Supercritical coal | 3.1 | 41800
[11 empty] | CCS - CCGT | 1.2 | 9000
[11 empty] | CCS - IGCC | 5.3 | 8900
[11 empty] | Biomass power plant (small) | 3.043 | 47600
[11 empty] | Biogas power plant (small) | 0.11 | 97000
[11 empty] | MSW incineration | 24.1437 | 243700
[11 empty] | Landfill | 13.5 | 125000
[11 empty] | Diesel power plant | 6.4 | 8000
[11 empty] | Batteries | 0 | 0

## Capex
This should be updated every project!. Could be used for Total system cost analysis or for populating Build Cost data |  |  | (urgency catalogue)
|  | DEA, 2020 | DEA,2023 | DEA, 2025 | DEA, 2030 | WACC | Economic life
DEA_Name | NREL_Name | Capex ($/kW) | Capex ($/kW) | Capex ($/kW) | Capex ($/kW) | (%) | years | 8%
Geothermal - large | Geothermal | 4000 |  |  | 4
Geothermal - small | #N/A | 5000 |  |  | 5 |  |  | DEA tech catalogue v12
Large hydro power plant | Hydro | 2080 |  |  | 2.08 |  |  | ws | technology | tech | type | input | size | cat | par | par_short | info | unit | priceyear | note | ref | est | year | val
Medium-small hydro power plant | #N/A | 2290 |  |  | 2.29 |  |  | 01 Coal CHP | Coal power plant, supercritical - extraction - coal - medium | Coal power plant, supercritical | extraction | coal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | J | [17, 18, 19, 20, 21, 22] | ctrl | 2020 | 1.9
Mini-micro hydro power plant | #N/A | 2700 |  |  | 2.7 |  |  | 02 LTE existing plant | Life time extension of coal extraction plant - refurbish - coal - large | Life time extension of coal extraction plant | refurbish | coal | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, F] | [4, 5, 6, 7] | ctrl | 2020 | 0.23577
Hydro pumped storage | PSH | 860 |  |  | 0.86 |  |  | 03a Coal to wood pellets exi bo | Rebuild extraction plant from coal to biomass a) existing boiler - fuel conversion - wood pellets - large | Rebuild extraction plant from coal to biomass a) existing boiler | fuel conversion | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E, K] | [10, 11, 12] | ctrl | 2020 | 0.5
Ground-mounted PV | Solar PV Utility | 0 |  |  | 0 |  |  | 03b Coal to wood chips n. boile | Rebuild extraction plant from coal to biomass b) new boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass b) new boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | [10, 12] | ctrl | 2020 | 1.6107
Rooftop PV | Solar PV Buildings | 0 |  |  | 0 |  |  | 03c coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass c) existing boiler - fuel conversion - wood chips - large | Rebuild extraction plant from coal to biomass c) existing boiler | fuel conversion | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 10 | ctrl | 2020 | 1.6107
Industrial PV | #N/A | 0 |  |  | 0 |  |  | 03d coal to wood chips exi. boi | Rebuild extraction plant from coal to biomass d) small coal boiler - fuel conversion - wood chips - small | Rebuild extraction plant from coal to biomass d) small coal boiler | fuel conversion | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  |  | ctrl | 2020
Floating PV | #N/A | 0 |  |  | 0 |  |  | 04 Gas turb. simple cycle, L | Gas turbine, simple cycle - back pressure - natural gas - large | Gas turbine, simple cycle | back pressure | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2020 | 0.59
Wind Onshore | Wind Onshore | 1500 |  |  | 1.5 |  |  | 04 Gas turb. simple cycle Sm-Me | Gas turbine, simple cycle - back pressure - natural gas - small | Gas turbine, simple cycle | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [6, 10] | ctrl | 2020 | 0.73
Small wind onshore | #N/A | 4000 |  |  | 4 |  |  | 04 Gas turb. simple cycle Micro | Gas turbine, simple cycle - back pressure - natural gas - micro | Gas turbine, simple cycle | back pressure | natural gas | micro | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [13, 14] | ctrl | 2020 | 1.2
Wind Offshore | Wind Offshore | 3500 |  |  | 3.5 |  |  | 05 Gas turb. CC, steam extract. | Gas turbine, combined cycle - extraction - natural gas - large | Gas turbine, combined cycle | extraction | natural gas | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 8] | ctrl | 2020 | 0.88
Tidal Impoundment | #N/A | 5500 |  |  | 5.5 |  |  | 05 Gas turb. CC, Back-pressure | Gas turbine, combined cycle - back pressure - natural gas - medium | Gas turbine, combined cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [5, 9] | ctrl | 2020 | 1.3
Tidal Stream | #N/A | 5300 |  |  | 5.3 |  |  | 06 Gas engines, natural gas | Engine - back pressure - natural gas - small | Engine | back pressure | natural gas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2020 | 0.95
Coal Subcritical | Coal | 1650 |  |  | 1.65 |  |  | 06 Gas engines, biogas | Engine - back pressure - biogas - small | Engine | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [3, 5, 11] | ctrl | 2020 | 0.95
Coal Supercritical | #N/A | 1400 |  |  | 1.4 |  |  | 08 WtE CHP, Large, 40 degree | Waste CHP, 40/80 degree - back pressure - waste - large | Waste CHP, 40/80 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 7.7557
Coal Ultra supercritical | #N/A | 1524.8 |  |  | 1.5248 |  |  | 08 WtE CHP, Large, 50 degree | Waste CHP, 50/100 degree - back pressure - waste - large | Waste CHP, 50/100 degree | back pressure | waste | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 8.5777
IGCC | IGCC | 2400 |  |  | 2.4 |  |  | 08 WtE CHP, Medium | Waste CHP - back pressure - waste - medium | Waste CHP | back pressure | waste | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 9.0213
CCGT | IGCC CCS | 690 |  |  | 0.69 |  |  | 08 WtE CHP, Small | Waste CHP - back pressure - waste - small | Waste CHP | back pressure | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | N | 1 | ctrl | 2020 | 10.3874
SCGT | OCGT | 772.8 |  |  | 0.7728 |  |  | 08 WtE HOP | Waste boiler - boiler - waste - small | Waste boiler | boiler | waste | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | P |  | ctrl | 2020 | 1.7399
CCS - Supercritical coal | Coal CCS | 1950 |  |  | 1.95 |  |  | 09a Wood Chips, Large 40 degree | Biomass CHP, 40/80 degree - back pressure - wood chips - large | Biomass CHP, 40/80 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.2873
CCS - CCGT | CCGT CCS | 1150 |  |  | 1.15 |  |  | 09a Wood Chips, Large 50 degree | Biomass CHP, 50/100 degree - back pressure - wood chips - large | Biomass CHP, 50/100 degree | back pressure | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.5346
CCS - IGCC | IGCC CCS | 950 |  |  | 0.95 |  |  | 09a Wood Chips, Medium | Biomass CHP - back pressure - wood chips - medium | Biomass CHP | back pressure | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.5432
Biomass power plant (small) | Biomass | 2000 |  |  | 2 |  |  | 09a Wood Chips, Small | Biomass CHP - back pressure - wood chips - small | Biomass CHP | back pressure | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2020 | 6.3177
Biogas power plant (small) | #N/A | 2150 |  |  | 2.15 |  |  | 09b Wood Pellets, Large 40 degr | Biomass CHP, 40/80 degree - back pressure - wood pellets - large | Biomass CHP, 40/80 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.2483
MSW incineration | #N/A | 0 |  |  | 0 |  |  | 09b Wood Pellets, Large 50 degr | Biomass CHP, 50/100 degree - back pressure - wood pellets - large | Biomass CHP, 50/100 degree | back pressure | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.3784
Landfill | #N/A | 2500 |  |  | 2.5 |  |  | 09b Wood Pellets, Medium | Biomass CHP - back pressure - wood pellets - medium | Biomass CHP | back pressure | wood pellets | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.0068
Diesel power plant | #N/A | 800 |  |  | 0.8 |  |  | 09b Wood Pellets, Small | Biomass CHP - boiler - wood pellets - small | Biomass CHP | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2020 | 6.0628
Batteries | Battery | 0 |  |  | 0 |  |  | 09c Straw, Large, 40 degree | Biomass CHP, 40/80 degree - back pressure - straw - large | Biomass CHP, 40/80 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.3813
Nuclear | Nuclear | #N/A |  |  | #N/A |  |  | 09c Straw, Large, 50 degree | Biomass CHP, 50/100 degree - back pressure - straw - large | Biomass CHP, 50/100 degree | back pressure | straw | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.6071
#N/A | Steam turbine (Gas/Oil) | #N/A |  |  | #N/A |  |  | 09c Straw, Medium | Biomass CHP - back pressure - straw - medium | Biomass CHP | back pressure | straw | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 3.5719
#N/A | Solar CSP | #N/A |  |  | #N/A |  |  | 09c Straw, Small | Biomass CHP - back pressure - straw - small | Biomass CHP | back pressure | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, J, K] | 1 | ctrl | 2020 | 6.6835
#N/A | Battery1H | [6 empty] | 09a Wood Chips HOP, small | Biomass boiler - boiler - wood chips - small | Biomass boiler | boiler | wood chips | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.69002
#N/A | Battery2H | [6 empty] | 09a Wood Chips HOP, medium | Biomass boiler - boiler - wood chips - medium | Biomass boiler | boiler | wood chips | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.4935
#N/A | Battery4H | [6 empty] | 09a Wood Chips HOP, large | Biomass boiler - boiler - wood chips - large | Biomass boiler | boiler | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.43941
#N/A | Battery8H | [6 empty] | 09b Wood Pellets HOP | Biomass boiler - boiler - wood pellets - small | Biomass boiler | boiler | wood pellets | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, L] |  | ctrl | 2020 | 0.71462
[8 empty] | 09c Straw HOP | Biomass boiler - boiler - straw - small | Biomass boiler | boiler | straw | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [F, K] |  | ctrl | 2020 | 0.87542
[8 empty] | 09a Wood Chips extract. plant | Biomass CHP - extraction - wood chips - large | Biomass CHP | extraction | wood chips | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.5
[8 empty] | 09b Wood Pellets extract. plant | Biomass CHP - extraction - wood pellets - large | Biomass CHP | extraction | wood pellets | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [J, K] | 1 | ctrl | 2020 | 2.15
[8 empty] | 10 Stirling | Stirling engine - back pressure - biomass - medium | Stirling engine | back pressure | biomass | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, E] | 1 | ctrl | 2020 | 3.8
[8 empty] | 11 SOFC-CHP | Solid oxide fuel cell - back pressure - biogas - small | Solid oxide fuel cell | back pressure | biogas | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [G, H, I, J] | [8, 13] | ctrl | 2020 | 3.3
[8 empty] | 12 LT-PEMFC CHP | Low temp PEM fuel cell - back pressure - hydrogen - small | Low temp PEM fuel cell | back pressure | hydrogen | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | B | [3, 4] | ctrl | 2020 | 1.3
[8 empty] | 20 Onshore turbines | Onshore wind turbine, utility - renewable power - wind - large | Onshore wind turbine, utility | renewable power | wind | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 |  | [16, 2, 4] | ctrl | 2020 | 1.1188
[8 empty] | 20 Domestic turbines | Onshore wind turbine, residential - renewable power - wind - small | Onshore wind turbine, residential | renewable power | wind | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [E, F] |  | ctrl | 2020 | 3.8
[8 empty] | 23 Wave Energy | Wave power - renewable power - wave - medium | Wave power | renewable power | wave | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [A, B] | [2, 2, 2, 3] | ctrl | 2020
[8 empty] | 40 Comp. hp, airsource 1 MW | Heat pump, air source - heat pump - electricity - small | Heat pump, air source | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 1.4271
[8 empty] | 40 Comp. hp, airsource 3 MW | Heat pump, air source - heat pump - electricity - medium | Heat pump, air source | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 0.95139
[8 empty] | 40 Comp. hp, airsource 10 MW | Heat pump, air source - heat pump - electricity - large | Heat pump, air source | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, K, L, P, Q] | [1, 14, 15] | ctrl | 2020 | 0.85625
[8 empty] | 40 Comp. hp, excess heat 1 MW | Heat pump, industrial excess heat - heat pump - electricity - small | Heat pump, industrial excess heat | heat pump | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 1.2368
[8 empty] | 40 Comp. hp, excess heat 3 MW | Heat pump, industrial excess heat - heat pump - electricity - medium | Heat pump, industrial excess heat | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.85625
[8 empty] | 40 Comp. hp, excess heat 10 MW | Heat pump, industrial excess heat - heat pump - electricity - large | Heat pump, industrial excess heat | heat pump | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.66597
[8 empty] | 40 Comp. hp, seawater 20 MW | Heat pump, sea water - heat pump - electricity - medium | Heat pump, sea water | heat pump | electricity | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, J, K, O] | [1, 14, 15] | ctrl | 2020 | 0.47569
[8 empty] | 40 Absorption heat pump, DH | Absorption heat pump - heat pump - heat - medium | Absorption heat pump | heat pump | heat | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [A, A1] | 3 | ctrl | 2020 | 0.564
[8 empty] | 44 Natural Gas DH Only | Gas boiler - boiler - natural gas - medium | Gas boiler | boiler | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | J | [2, 3] | ctrl | 2020 | 0.06
[8 empty] | 45.1.a Geothermal DH, 1200m, E | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.7138
[8 empty] | 45.1.b Geothermal DH, 2000m, E | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.8828
[8 empty] | 45.2.a Geothermal DH, 1200m, A | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 1200 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 1.2645
[8 empty] | 45.2.b Geothermal DH, 2000m, A | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - medium | Geothermal plant, absorption heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.0946
[8 empty] | 45.3.a Geoth. DH, 1200m, E (LT) | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000 m, dh temp 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.6988
[8 empty] | 45.3.b Geoth DH, 2000m, E (LT) | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree - renewable heat - geothermal - medium | Geothermal plant, electric heat pump, 2000m. DH temperature 70/35 degree | renewable heat | geothermal | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, K] | [2, 4, 7] | ctrl | 2020 | 2.8756
[8 empty] | 46 Solar District Heating | Solar DH - renewable heat - solar - medium | Solar DH | renewable heat | solar | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 | [C, E, H, N, S] | [16, 18] | ctrl | 2020 | 0.30565
[8 empty] | 50 Diesel engine farm | Engine, peak plant - back pressure - diesel - medium | Engine, peak plant | back pressure | diesel | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [1, 6, 9, 10] | ctrl | 2020 | 0.343
[8 empty] | 51 Natural gas engine plant | Engine, peak plant - back pressure - natural gas - medium | Engine, peak plant | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [L, M, N, R] | [7, 5, 9] | ctrl | 2020 | 0.4947
[8 empty] | 52 OCGT - Natural gas | Gas turbine, open cycle - back pressure - natural gas - medium | Gas turbine, open cycle | back pressure | natural gas | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [M, N, O] | [7, 9, 10] | ctrl | 2020 | 0.45396
[8 empty] | 52 OCGT - Light fuel oil | Gas turbine, open cycle - back pressure - light fuel oil - medium | Gas turbine, open cycle | back pressure | light fuel oil | medium | Financial data | Nominal investment (*total) [2015-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2015 | [C, D] | 19 | ctrl | 2020 | 0.3783
[8 empty] | 41 Electric boiler, small | Electric boiler - boiler - electricity - small | Electric boiler | boiler | electricity | small | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.15
[8 empty] | 41 Electric boiler, large | Electric boiler - boiler - electricity - large | Electric boiler | boiler | electricity | large | Financial data | Nominal investment (*total) [2015-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2015 |  |  | ctrl | 2020 | 0.07
[8 empty] | 22 Rooftop PV residential | PV - renewable power - solar - residential rooftop | PV | renewable power | solar | residential rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2020 | 1.2419
[8 empty] | 22 Rooftop PV commercial | PV - renewable power - solar - commercial/industrial rooftop | PV | renewable power | solar | commercial/industrial rooftop | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,O | 2, 4 | ctrl | 2020 | 0.87231
[8 empty] | 22 Utility-scale PV | PV - renewable power - solar - utility-scale, ground mounted | PV | renewable power | solar | utility-scale, ground mounted | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.5625
[8 empty] | 22 Utility-scale PV tracker | PV - renewable power - solar - utility-scale ground mounted, single axis tracking | PV | renewable power | solar | utility-scale ground mounted, single axis tracking | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | M,N,O,Q | 2, 4 | ctrl | 2020 | 0.65035
[8 empty] | 40 co2. hp, seawater 50-100 MW | Heat pump, sea water, co2, 65 MW - heat pump - electricity - large | Heat pump, sea water, co2, 65 MW | heat pump | electricity | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | A, M, R | 1 | ctrl | 2020 | 0.93564
[8 empty] | 45.4 Geothermal DH, lar scale | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree - renewable heat - geothermal - large | Geothermal plant, electric heat pump, 2000 m, dh temp 80/40 degree | renewable heat | geothermal | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_h] | Nominal investment | *total | MEUR/MW_h | 2020 | C,K | 2, 4, 7 | ctrl | 2020 | 1.3412
[8 empty] | 21 Offshore turbines | Offshore wind turbines - renewable power - wind - large | Offshore wind turbines | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2020 | 2.1159
[8 empty] | 21 Near shore turbines | Offshore wind turbines, nearshore - renewable power - wind - large | Offshore wind turbines, nearshore | renewable power | wind | large | Financial data | Nominal investment (*total) [2020-MEUR/MW_e] | Nominal investment | *total | MEUR/MW_e | 2020 | F | 3 | ctrl | 2020 | 1.6999

## RampCosts
FROM: Intertech/APTEK - NREL (Kumar et al)
UNITS | USD/MW | USD/MW
NAME | Ramp up charge | Ramp down charge
Coal lignite | 3.5 | 3.5
Coal subcritical | 3.5 | 3.5
Coal supercritical | 3.2667 | 3.2667
Coal ultrasupercritical | 3.2667 | 3.2667
IGCC | 3.2667 | 3.2667
CCGT | 1.6 | 1.6
Steam turbine (Gas/Oil) | 3 | 3 |  | Technology | Coal- small sub critical | Coal - large sub critical | Coal - super critical | Gas - CC (GT+HRSG+ST) | Gas - Large Frame CT | Gas - Aero Derivative CT | Gas - Steam | References
OCGT | 2.9444 | 2.9444 |  | median lower bound cost (/Mwcap) | 3.34 | 2.45 | 1.96 | 0.64 | 1.59 | 0.63 | 1.92 | https://www.nrel.gov/docs/fy12osti/55433.pdf
Nuclear | 3.2667 | 3.2667 |  | range of load follow (fraction cap) | 0.32 | 0.35 | 0.3 | 0.2 | 0.27 | 0.2 | 0.32 | https://www.nrel.gov/docs/fy13osti/55588.pdf
Hydro RoR | 0 | 0 | <<Changed from 0.05. Should rather be zero for the scaling issue | ramp up/ down charge per MW | 5.2188 | 3.5 | 3.2667 | 1.6 | 2.9444 | 1.575 | 3
Hydro RoRpondage | 0 | 0
Hydro Reservoir | 0 | 0
Hydro PSH | 0 | 0
Battery | 0 | 0
Solid biomass | 3.2667 | 3.2667
Biogas | 2.9444 | 2.9444
Geothermal | 3.2667 | 3.2667

## AuxDemand
SOURCE: Marco Borini (ex-WEO)
NAME | DeratingFactor
Coal lignite | 0.94
Coal subcritical | 0.94
Coal supercritical | 0.94
Coal ultrasupercritical | 0.94
IGCC | 0.94
CHP Other | 0.94
CCGT | 0.96
Steam turbine (Gas/Oil) | 0.96
OCGT | 0.96
Fuel cell | 1
Nuclear | 0.94
Hydro RoR | 0.99
Hydro RoRpondage | 0.99
Hydro Reservoir | 0.99
Solid biomass | 0.94
Biogas | 0.94
Geothermal | 0.94
Wind onshore | 0.99
Wind offshore | 0.99
Solar PV Utility | 0.99
Solar PV Buildings | 0.99
Solar CSP | 0.97
Ocean energy | 0.99
Hydro PSH | 0.99
Hydro RoR | 0.99
Hydro RoRpondage | 0.99
Hydro Reservoir | 0.99
CHP Coal | 0.94
CHP Gas | 0.96
CHP Oil | 0.96
Battery | 1
Hydro Pondage | 0.99
Direct_inputs | 1

## MFOR
adjusted to match WEO who use 5% for all non-CHP elec
|  | Source: acil allen | [8 empty] | Maintenance events per year: | 2
| UNITS | % annual | hours | % annual | hours | % annual | hours | % capacity | % annual | hours | days |  | Notes |  |  |  | Source: DEA Indonesia, FOR/maintenance rate |  |  |  | % capacity
DEA Name | NAME | POR | MTTR_POR | FFOR | MTTR_FFOR | PFOR | MTTR_PFOR | partial derating | TFOR | MTTR_TFOR | maintenance days per year | effective forced outage rate for all plants | Notes | EAF | POR | MTTR_POR | FOR | MTTR_FFOR | PFOR | MTTR_PFOR | partial derating | EAF
Coal Subcritical | Coal lignite | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 |  | 87.4808 | 11.5385 | 504 | 7 | 50 | 0 | 24 | #N/A | 81.4615
Coal Subcritical | Coal subcritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 |  | 87.4808 | 11.5385 | 504 | 7 | 50 | 0 | 24 | #N/A | 81.4615 |  | Source: acil allen |  | Maintenance events per year:
Coal Supercritical | Coal supercritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 | ** using coal | 87.4808 | 13.4615 | 588 | 7 | 50 | 0 | 24 | #N/A | 79.5385 |  |  |  | 2
Coal Ultra supercritical | Coal ultrasupercritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 |  | 87.4808 | 13.4615 | 588 | 7 | 50 | 0 | 24 | #N/A | 79.5385 |  | UNITS | % annual | hours | % annual | hours | % annual | hours | % capacity | days
IGCC | IGCC | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 | ** based on coal | 87.4808 | 12.6923 | 554.4 | 5.53 | 50 | 0 | 24 | #N/A | 81.7777 |  | NAME | POR | MTTR_POR | FFOR | MTTR_FFOR | PFOR | MTTR_PFOR | partial derating | maintenance days per year
CCGT | CCGT | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 4.3 | 17 | 20 | 4.5 |  | 90.0205 | 9.6154 | 420 | 5 | 17 | 0 | 24 | #N/A | 85.3846 |  | Gas CCGT | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 20
Steam turbine (Gas/Oil) | Steam turbine (Gas/Oil) | 8.2192 | 360 | 2 | 30 | 1 | 27 | 40 | 2.3 | 30 | 30 | 2.4 | partial to available estimate was strangely high (1240) so used same as for full outage | 89.3808 | 0 | 0 | 0 | 30 | 0 | 24 | #N/A | 100 |  | Gas OCGT | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 3
SCGT | OCGT | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 2.3 | 30 | 3 | 2.4 | partial to available estimate was strangely high (1240) so used same as for full outage | 96.7781 | 5.7692 | 252 | 2 | 30 | 0 | 24 | #N/A | 92.2308 |  | Steam turbine (Gas/Oil) | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30 | ** using coal
Nuclear | Nuclear | 0.10959 | 960 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 |  | 95.5904 | 0 | 0 | 0 | 50 | 0 | 24 | #N/A | 100 |  | Coal supercritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30
Biomass power plant (small) | Solid biomass | 8.2192 | 360 | 3 | 50 | 10 | 20 | 30 | 6 | 50 | 30 | 6 |  | 85.7808 | 11.5385 | 504 | 7 | 50 | 0 | 24 | #N/A | 81.4615 |  | Nuclear Light Water | 8.2192 | 360 | 2.5 | 100 | 6 | 40 | 30 | 30 | ** based on coal
Mini-micro hydro power plant | Hydro RoR | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 4.1 | 18 | 7 | 4.1 |  | 93.9822 | 11.5385 | 504 | 4 | 18 | 0 | 24 | #N/A | 84.4615 |  | Solid biomass | 8.2192 | 360 | 3 | 50 | 10 | 20 | 30 | 30
Medium-small hydro power plant | Hydro RoRpondage | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 4.1 | 18 | 7 | 4.1 |  | 93.9822 | 11.5385 | 504 | 4 | 18 | 0 | 24 | #N/A | 84.4615 |  | Hydro with pondage | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7 | partial to available estimate was strangely high (1240) so used same as for full outage
Large hydro power plant | Hydro Reservoir | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 4.1 | 18 | 7 | 4.1 |  | 93.9822 | 11.5385 | 504 | 4 | 18 | 0 | 24 | #N/A | 84.4615 |  | Hydro with reservoir | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7 | partial to available estimate was strangely high (1240) so used same as for full outage
Hydro pumped storage | Hydro PSH | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 4.1 | 18 | 7 | 4.1 |  | 93.9822 | 5.7692 | 252 | 4 | 18 | 0 | 24 | #N/A | 90.2308
CHP Coal | CHP Coal | 6 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 |  | 89.7 | 0 | 24 | 0 | 24 | 0 | 24 | #N/A | 100
CHP Oil | CHP Oil | 6 | 360 | 2 | 30 | 1 | 27 | 30 | 2.3 | 30 | 30 | 2.3 |  | 91.7 | 0 | 24 | 0 | 24 | 0 | 24 | #N/A | 100
CHP Gas | CHP Gas | 6 | 360 | 2 | 30 | 1 | 27 | 30 | 2.3 | 30 | 30 | 2.3 |  | 91.7 | 0 | 24 | 0 | 24 | 0 | 24 | #N/A | 100 |  | Source: acil allen |  | Maintenance events per year:
CHP Nuclear | CHP Nuclear | 6 | 360 | 2.5 | 50 | 6 | 20 | 30 | 4.3 | 50 | 30 | 4.3 |  | 89.7 | 0 | 24 | 0 | 24 | 0 | 24 | #N/A | 100 |  |  |  | 2
CHP Other | CHP Other | 6 | 360 | 3.5 | 50 | 6 | 20 | 30 | 5.3 | 50 | 30 | 5.3 |  | 88.7 | 0 | 24 | 0 | 24 | 0 | 24 | #N/A | 100 |  | UNITS | % annual | hours | % annual | hours | % annual | hours | % capacity | days
Geothermal - large | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 7.6923 | 336 | 10 | 50 | 0 | 24 | #N/A | 82.3077 | **assumed | NAME | POR | MTTR_POR | FFOR | MTTR_FFOR | PFOR | MTTR_PFOR | partial derating | maintenance days per year
Geothermal - small | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 7.6923 | 336 | 10 | 50 | 0 | 24 | #N/A | 82.3077 | **assumed | Coal lignite | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30
Wind Onshore | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0.30769 | 13.44 | 0.025 | 6 | 0 | 24 | #N/A | 99.6673 | **assumed | Coal subcritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30
Small wind onshore | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0.30769 | 13.44 | 0.03 | 6 | 0 | 24 | #N/A | 99.6623 | **assumed | Coal supercritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30 | ** using coal
Wind Offshore | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0.30769 | 13.44 | 0.04 | 6 | 0 | 24 | #N/A | 99.6523 | **assumed | Coal ultrasupercritical | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30
Tidal Impoundment | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0 | 0 | 0.04 | 6 | 0 | 24 | #N/A | 99.96 | **assumed | IGCC | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30 | ** based on coal
Tidal Stream | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0 | 0 | 0.04 | 6 | 0 | 24 | #N/A | 99.96 | **assumed | CCGT | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 20
CCS - Supercritical coal | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0 | 0 | 7 | 50 | 0 | 24 | #N/A | 93 | **assumed | Steam turbine (Gas/Oil) | 8.2192 | 360 | 2 | 30 | 1 | 27 | 40 | 30 | partial to available estimate was strangely high (1240) so used same as for full outage
CCS - CCGT | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0 | 0 | 5 | 17 | 0 | 24 | #N/A | 95 | **assumed | OCGT | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 3 | partial to available estimate was strangely high (1240) so used same as for full outage
CCS - IGCC | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0 | 0 | 6 | 50 | 0 | 24 | #N/A | 94 | **assumed | Nuclear | 8.2192 | 360 | 2.5 | 50 | 6 | 20 | 30 | 30
Biogas power plant (small) | Biogas | 5.4795 | 240 | 4 | 17 | 1 | 15 | 50 | 4.3 | 17 | 20 | 4.5 | 0 | 90.0205 | 9.6154 | 420 | 5 | 50 | 0 | 24 | #N/A | 85.3846 | **assumed | Hydro_RoR | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7
MSW incineration | #N/A | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 2.3 | 30 | 3 | 2.4 | partial to available estimate was strangely high (1240) so used same as for full outage | 96.7781 | 5.5769 | 243.6 | 0.01 | 50 | 0 | 24 | #N/A | 94.4131 | **assumed | Hydro_RoRpondage | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7
Landfill | #N/A | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 2.3 | 30 | 3 | 2.4 | partial to available estimate was strangely high (1240) so used same as for full outage | 96.7781 | 9.6154 | 420 | 5 | 50 | 0 | 24 | #N/A | 85.3846 | **assumed | Hydro_Reservoir | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7
Diesel power plant | #N/A | 0.82192 | 36 | 2 | 30 | 1 | 27 | 40 | 2.3 | 30 | 3 |  |  |  | 1.5385 | 67.2 | 3 | 30 | 0 | 24 | #N/A | 95.4615 | **assumed | Hydro_PSHa_SR | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7
Batteries | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A |  | #N/A | 0.38462 | 16.8 | 0.38 | 12 | 0 | 24 | #N/A | 99.2354 | **assumed | Hydro_PSHb_WR | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7
[24 empty] | Hydro_PSHc_ER | 1.9178 | 84 | 3.5 | 18 | 2 | 18 | 30 | 7
Use OCGT/etc in absence of other data
| Original | [22 empty] | Source: DEA Indonesia, FOR/maintenance rate | FOR | POR | Maintenance (weeks/yr)
| UNITS | % annual | hours | % annual | [19 empty] | Geothermal - large | 10 | 7.6923 | 4
| NAME | POR | MTTR_POR | FFOR | [19 empty] | Geothermal - small | 10 | 7.6923 | 4
| Coal lignite | 8.2192 | 360 | 2.5 | [19 empty] | Large hydro power plant | 4 | 11.5385 | 6
| Coal subcritical | 8.2192 | 360 | 2.5 | [19 empty] | Medium-small hydro power plant | 4 | 11.5385 | 6
| Coal supercritical | 8.2192 | 360 | 2.5 | [19 empty] | Mini-micro hydro power plant | 4 | 11.5385 | 6
| Coal ultrasupercritical | 8.2192 | 360 | 2.5 | [19 empty] | Hydro pumped storage | 4 | 5.7692 | 3
| IGCC | 8.2192 | 360 | 2.5 | [19 empty] | Wind Onshore | 0.025 | 0.30769 | 0.16
| CCGT | 5.4795 | 240 | 4 | [19 empty] | Small wind onshore | 0.03 | 0.30769 | 0.16
| Steam turbine (Gas/Oil) | 8.2192 | 360 | 2 | [19 empty] | Wind Offshore | 0.04 | 0.30769 | 0.16
| OCGT | 0.82192 | 36 | 2 | [19 empty] | Tidal Impoundment | 0.04 | 0 | 0
| Nuclear | 8.2192 | 360 | 2.5 | [19 empty] | Tidal Stream | 0.04 | 0 | 0
| Hydro RoR | 1.9178 | 84 | 3.5 | [19 empty] | Coal Subcritical | 7 | 11.5385 | 6
| Hydro RoRpondage | 1.9178 | 84 | 3.5 | [19 empty] | Coal Supercritical | 7 | 13.4615 | 7
| Hydro Reservoir | 1.9178 | 84 | 3.5 | [19 empty] | Coal Ultra supercritical | 7 | 13.4615 | 7
| Hydro PSH | 1.9178 | 84 | 3.5 | [19 empty] | IGCC | 5.53 | 12.6923 | 6.6
| CHP Coal | 8.2192 | 360 | 2.5 | [19 empty] | CCGT | 5 | 9.6154 | 5
| CHP Oil | 8.2192 | 360 | 2 | [19 empty] | SCGT | 2 | 5.7692 | 3
| CHP Gas | 0.82192 | 36 | 2 | [19 empty] | CCS - Supercritical coal | 7 | 0 | 0
| CHP Nuclear | 8.2192 | 360 | 2.5 | [19 empty] | CCS - CCGT | 5 | 0 | 0
[24 empty] | CCS - IGCC | 6 | 0 | 0
[24 empty] | Biomass power plant (small) | 7 | 11.5385 | 6
[24 empty] | Biogas power plant (small) | 5 | 9.6154 | 5
[24 empty] | MSW incineration | 0.01 | 5.5769 | 2.9
[24 empty] | Landfill | 5 | 9.6154 | 5
[24 empty] | Diesel power plant | 3 | 1.5385 | 0.8
[24 empty] | Batteries | 0.38 | 0.38462 | 0.2
Note on C13: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://analysesetdonnees.rte-france.com/en/generation/nuclear Reply: This is the annual. There is also every 3-4 years and every 10 years, whereby nuclear is offline for more extended periods

## CapFactors
DEA_Tech | Technology | RatingFactor | RatingFactor_NZE2030 | RatingFactor_NZE2050 | MaxCapFacDay | MaxCapFacMonth | Firm Capacity |  | Source: DEA Indonesia, CF incl. outages
Mini-micro hydro power plant | Hydro RoR | 0.75885 | 0.39258 | 0.39258 | #N/A | #N/A | 0.75885 |  | Technology | RatingFactor | MaxCapFacDay | MaxCapFacMonth
Medium-small hydro power plant | Hydro RoRpondage | 0.75885 | 0.39258 | 0.39258 | 0.75885 | #N/A | 0.75885 |  | Geothermal - large | 80 | 80 | 80
Large hydro power plant | Hydro Reservoir | 0.35885 | 0.37909 | 0.31926 | #N/A | 0.35885 | 0.35885 |  | Geothermal - small | 80 | 80 | 80
Biomass power plant (small) | Solid biomass | 0.6 | 0.77241 | 0.85625 | #N/A | #N/A | 0.6 |  | Large hydro power plant | 35.8846 | 35.8846 | 35.8846
#N/A | Biomass Cofiring | 0.6 | 0.77241 | 0.68736 | #N/A | #N/A | 0.6 |  | Medium-small hydro power plant | 75.8846 | 75.8846 | 75.8846
Biogas power plant (small) | Biogas | 0.6 | 0.61403 | 0.68795 | #N/A | #N/A | 0.6 |  | Mini-micro hydro power plant | 75.8846 | 75.8846 | 75.8846
Geothermal - large | Geothermal | 0.8 | 0.82259 | 0.84939 | #N/A | #N/A | 0.8 |  | Ground-mounted PV | 19.4064 | 19.4064 | 19.4064
Wind Onshore | Wind onshore | 0.3402 | 0.3402 | 0.3402 | #N/A | #N/A | 0.3402 |  | Rooftop PV | 17.6941 | 17.6941 | 17.6941
Wind Offshore | Wind offshore | 0.47852 | 0.47852 | 0.47852 | #N/A | #N/A | 0.47852 |  | Industrial PV | 17.6941 | 17.6941 | 17.6941
Ground-mounted PV | Solar PV Utility | 0.19406 | 0.19406 | 0.19406 | #N/A | #N/A | 0 |  | Floating PV | 20.9589 | 20.9589 | 20.9589
Rooftop PV | Solar PV Buildings | 0.17694 | 0.17694 | 0.17694 | #N/A | #N/A | 0 |  | Wind Onshore | 34.02 | 34.02 | 34.02
#N/A | Solar CSP | 0.34 | 0.34 | 0.34 | 0.34 | #N/A | 0.34 | **filler values | Small wind onshore | 33.8455 | 33.8455 | 33.8455
Tidal Stream | Ocean energy | 0.33 | 0.33 | 0.33761 | #N/A | #N/A | 0.33 |  | Wind Offshore | 47.8523 | 47.8523 | 47.8523
#N/A | CHP Coal | 0.4 | 0.4 | 0.4 | #N/A | #N/A | 0.4 | **filler values | Tidal Impoundment | 0 | 0 | 0
#N/A | CHP Oil | 0.4 | 0.4 | 0.4 | #N/A | #N/A | 0.4 | **filler values | Tidal Stream | 33 | 33 | 33
#N/A | CHP Gas | 0.4 | 0.4 | 0.4 | #N/A | #N/A | 0.4 | **filler values
#N/A | CHP Other | 0.6 | 0.6 | 0.6 | #N/A | #N/A | 0.6 | **filler values | Source: DEA Indonesia, CF theoretical, excl. outages
Geothermal - small | #N/A | 0.6 | 0.6 | 0.6 | #N/A | #N/A | 0.6 | **filler values | Technology | RatingFactor | MaxCapFacDay | MaxCapFacMonth
[9 empty] | Geothermal - large | 90 | 90 | 90
[9 empty] | Geothermal - small | 90 | 90 | 90
[9 empty] | Large hydro power plant | 40 | 40 | 40
[9 empty] | Medium-small hydro power plant | 80 | 80 | 80
[9 empty] | Mini-micro hydro power plant | 80 | 80 | 80
[9 empty] | Ground-mounted PV | 19.4064 | 19.4064 | 19.4064
[9 empty] | Rooftop PV | 17.6941 | 17.6941 | 17.6941
[9 empty] | Industrial PV | 17.6941 | 17.6941 | 17.6941
[9 empty] | Floating PV | 20.9589 | 20.9589 | 20.9589
[9 empty] | Wind Onshore | 35 | 35 | 35
[9 empty] | Small wind onshore | 35 | 35 | 35
[9 empty] | Wind Offshore | 50 | 50 | 50
[9 empty] | Tidal Impoundment | 35 | 35 | 35
[9 empty] | Tidal Stream | 33 | 33 | 33

## DEA_IDN_Generator_Props
Source (DEA, 2021) Generation technology database for Indonesia
2020 | Geothermal - large | Geothermal - small | Large hydro power plant | Medium-small hydro power plant | Mini-micro hydro power plant | Hydro pumped storage | Ground-mounted PV | Rooftop PV | Industrial PV | Floating PV | Wind Onshore | Small wind onshore | Wind Offshore | Tidal Impoundment | Tidal Stream | Coal Subcritical | Coal Supercritical | Coal Ultra supercritical | IGCC | CCGT | SCGT | CCS - Supercritical coal | CCS - CCGT | CCS - IGCC | Biomass power plant (small) | Biogas power plant (small) | MSW incineration | Landfill | Diesel power plant | Batteries
Generating capacity for one unit (MWe) | 55 | 10 | 150 | 50 | 5 | 250 |  |  |  |  | 3.5 | 0.85 | 8 | 1 | 1 | 150 | 600 | 1000 | 150-200 | 600 | 50 | -60 | -40 | -65 | 25 | 1 | 21.5896 | 1 | 20
Generating capacity for total power plant (MWe) | 110 | 20 | 150 | 50 | 5 | 1000 |  |  |  | 10 | 70 | 12.75 | 240 | 30 | 10 | 150 | 600 | 1000 | 600 | 600 | 100 | -60 | -40 | -65 | 25 | 1 | 21.5896 | 1 | 100
Electricity efficiency, net (%), name plate | 16 | 10 | 95 | 95 | 80 | 80 | - | - | - | - | 100 | 100 | 100 | 90 | 90 | 34.83 | 37.67 | 42.5 | 42 | 57 | 33.5 | -7 | -7 | -7 | 32 | 35 | 0.29 | 35 | 46
Electricity efficiency, net (%), annual average | 15 | 10 | 95 | 95 | 80 | 80 | - | - | - | - | 100 | 100 | 100 | 90 | 90 | 34.33 | 36.67 | 41.5 | 40 | 56 | 32.5 | -8 | -8 | -8 | 31 | 34 | 0.2755 | 34 | 45
Forced outage (%) | 10 | 10 | 4 | 4 | 4 | 4 | - | - | - | - | 0.025 | 0.03 | 0.04 | 0.04 | 0.04 | 7 | 7 | 7 | 5.53 | 5 | 2 | 7 | 5 | 6 | 7 | 5 | 0.01 | 5 | 3 | 0.38
Maintenance rate (%) | 7.6923 | 7.6923 | 11.5385 | 11.5385 | 11.5385 | 5.7692 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.30769 | 0.30769 | 0.30769 | 0 | 0 | 11.5385 | 13.4615 | 13.4615 | 12.6923 | 9.6154 | 5.7692 | 0 | 0 | 0 | 11.5385 | 9.6154 | 5.5769 | 9.6154 | 1.5385 | 0.38462
Planned outage (weeks per year) | 4 | 4 | 6 | 6 | 6 | 3 | - | - | - | - | 0.16 | 0.16 | 0.16 |  |  | 6 | 7 | 7 | 6.6 | 5 | 3 |  |  |  | 6 | 5 | 2.9 | 5 | 0.8 | 0.2
Technical lifetime (years) | 30 | 30 | 50 | 50 | 50 | 50 | 35 | 35 |  |  | 27 | 27 | 27 | 40 | 25 | 30 | 30 | 30 | 30 | 25 | 25 |  | - | - | 25 | 25 | 25 | 25 | 25 | 20
Construction time (years) | 2 | 2 | 4 | 3 | 2 | 4.3 | 0.5 | 0.1 |  |  | 1.5 | 1 | 3 | 5 | 3 | 3.25 | 3.75 | 4.33 | 4 | 2.5 | 1.5 |  |  |  | 2 | 1.5 | 2.5 | 1.5 | 1 | 0.2
Space requirement (1000 m2/MWe) | 30 | 30 | 62 | 14 |  | 30 |  |  | 9 | 14 | 14 | 58 | 185 | 0.2 |  | - | - | - | - | - | 0.02 |  |  | - | 35 | 70 | 1.5 |  | 0.05
Capacity factor (%), theoretical | 90 | 90 | 40 | 80 | 80 | - | 19.4064 | 17.6941 | 17.6941 | 20.9589 | 35 | 35 | 50 | 35 | 33 | - | - | - | - | - | - |  | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 80 | 80 | 35.8846 | 75.8846 | 75.8846 | - | 19.4064 | 17.6941 | 17.6941 | 20.9589 | 34.02 | 33.8455 | 47.8523 |  | 33 | - | - | - | - | - | - |  | - | - | - | - | - | - | -
Ramping (% per minute) | 3 |  | 50 | 50 | - | 50 | - | - | - | - | - | - | - | 50 | - | 3.5 | 4 | 5 | 3 | 20 | 20 | 4 | 20 | 3 | 10 | 20 | 10 |  | 25
Minimum load (% of full load) |  |  | 0 | 0 | - | 0 | - | - | - | - | - | - | - | 0 | - | 30 | 25 | 30 | 50 | 45 | 20 | 30 | 45 | 50 | 30 | 20 | 20 |  | 6
Warm start-up time (hours) |  |  | 0.1 | 0.1 | - | 0.1 | - | - | - | - | - | - | - | 0.1 | - | 3 | 4 | 4 | 6 | 2 | 0.25 | 4 | 2 | 6 | 0.5 |  | 0.5 |  | 0.05
Cold start-up time (hours) |  |  | 0.1 | 0.1 | - | 0.1 | - | - | - | - | - | - | - | 0.1 | - | 8 | 12 | 12 | 15-80 | 4 | 0.5 | 12 | 4 | 15-80 | 10 |  | 2 |  | 0.3
PM 2.5 (gram per Nm3) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 19.6
SO2 (degree of desulphuring, %) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 73 | 73 | 99 | - | - | 97 | 99 | 99 | 0 |  |  |  | 0
NOX (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.5 | 262.5 | 262.5 | 173 | 86.4 | 86.4 | 263 | 80 | 173 | 125 |  |  |  | 280
CH4 (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - |  | - | - |  | - |  | 0.94
N2O (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - |  | - | - |  | - |  | 1.1
Nominal investment (M$/MWe) | 4 | 5 | 2.08 | 2.29 | 2.7 | 0.86 |  |  |  |  | 1.5 | 4 | 3.5 | 5.5 | 5.3 | 1.65 | 1.4 | 1.5248 | 2.4 | 0.69 | 0.7728 | 1.95 | 1.15 | 0.95 | 2 | 2.15 |  | 2.5 | 0.8
- of which equipment | 0.6 | 0.6 | 0.3 | 0.3 | 0.3 |  | 0.44444 | 0.44444 | 0.44444 | 0.50617 | 0.65 | 0.55 | 0.45 |  | 0.87 | [9 empty] | 65 | 65 | 4.012 | 0.72
- of which installation | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 |  | 0.55556 | 0.55556 | 0.55556 | 0.49383 | 0.35 | 0.45 | 0.55 |  | 0.13 | [9 empty] | 35 | 35 | 2.788 | 0.28
Fixed O&M ($/MWe/year) | 50000 | 65000 | 37700 | 41900 | 53000 | 8000 | 14400 | 14400 | 14400 | 16200 | 60000 | 73200 | 72600 | 70800 | 283000 | 45300 | 41200 | 56600 | 60000 | 23500 | 23200 | 41800 | 9000 | 8900 | 47600 | 97000 | 243700 | 125000 | 8000
Variable O&M ($/MWh) | 0.25 | 0.37 | 0.65 | 0.5 | 0.5 | 1.325 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 11.7257 | 0.125 | 0.12 | 0.11 | 12 | 2.3 |  | 3.1 | 1.2 | 5.3 | 3.043 | 0.11 | 24.1437 | 13.5 | 6.4
Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 110 | 50 | 50 | 100 | 80 | 24
2030 | Geothermal - large | Geothermal - small | Large hydro power plant | Medium-small hydro power plant | Mini-micro hydro power plant | Hydro pumped storage | Ground-mounted PV | Rooftop PV | Industrial PV | Floating PV | Wind Onshore | Small wind onshore | Wind Offshore | Tidal Impoundment | Tidal Stream | Coal Subcritical | Coal Supercritical | Coal Ultra supercritical | IGCC | CCGT | SCGT | CCS - Supercritical coal | CCS - CCGT | CCS - IGCC | Biomass power plant (small) | Biogas power plant (small) | MSW incineration | Landfill | Diesel power plant | Batteries
Generating capacity for one unit (MWe) | 55 | 10 | 150 | 50 | 5 | 250 |  |  |  |  | 3.5 | 0.85 | 8 | 1 | 1 | 150 | 600 | 1000 | 150-200 | 600 | 50 | -60 | -40 | -65 | 25 | 1 | 21.5896 | 1 | 20
Generating capacity for total power plant (MWe) | 110 | 20 | 150 | 50 | 5 | 1000 |  |  |  | 10 | 70 | 12.75 | 240 | 30 | 10 | 150 | 600 | 1000 | 600 | 600 | 100 | -60 | -40 | -65 | 25 | 1 | 21.5896 | 1 | 100
Electricity efficiency, net (%), name plate | 16 | 10 | 95 | 95 | 80 | 80 | - | - | - | - | 100 | 100 | 100 | 90 | 90 | 34.83 | 37.67 | 42.5 | 42 | 57 | 33.5 | -7 | -7 | -7 | 32 | 35 | 0.29 | 35 | 46
Electricity efficiency, net (%), annual average | 15 | 10 | 95 | 95 | 80 | 80 | - | - | - | - | 100 | 100 | 100 | 90 | 90 | 34.33 | 36.67 | 41.5 | 40 | 56 | 32.5 | -8 | -8 | -8 | 31 | 34 | 0.2755 | 34 | 45
Forced outage (%) | 10 | 10 | 4 | 4 | 4 | 4 | - | - | - | - | 0.025 | 0.03 | 0.04 | 0.04 | 0.04 | 7 | 7 | 7 | 5.53 | 5 | 2 | 7 | 5 | 6 | 7 | 5 | 0.01 | 5 | 3 | 0.38
Maintenance rate (%) |  | 7.6923 | 11.5385 | 11.5385 | 11.5385 | 5.7692 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.30769 | 0.30769 | 0.30769 | 0 | 0 | 11.5385 | 13.4615 | 13.4615 | 12.6923 | 9.6154 | 5.7692 | 0 | 0 | 0 | 11.5385 | 9.6154 | 5.5769 | 9.6154 | 1.5385 | 0.38462 | 0
Planned outage (weeks per year) | 4 | 4 | 6 | 6 | 6 | 3 | - | - | - | - | 0.16 | 0.16 | 0.16 |  |  | 6 | 7 | 7 | 6.6 | 5 | 3 |  |  |  | 6 | 5 | 2.9 | 5 | 0.8 | 0.2
Technical lifetime (years) | 30 | 30 | 50 | 50 | 50 | 50 | 35 | 35 |  |  | 27 | 27 | 27 | 40 | 25 | 30 | 30 | 30 | 30 | 25 | 25 |  | - | - | 25 | 25 | 25 | 25 | 25 | 20
Construction time (years) | 2 | 2 | 4 | 3 | 2 | 4.3 | 0.5 | 0.1 |  |  | 1.5 | 1 | 3 | 5 | 3 | 3.25 | 3.75 | 4.33 | 4 | 2.5 | 1.5 |  |  |  | 2 | 1.5 | 2.5 | 1.5 | 1 | 0.2
Space requirement (1000 m2/MWe) | 30 | 30 | 62 | 14 |  | 30 |  |  | 9 | 14 | 14 | 58 | 185 | 0.2 |  | - | - | - | - | - | 0.02 |  |  | - | 35 | 70 | 1.5 |  | 0.05
Capacity factor (%), theoretical | 90 | 90 | 40 | 80 | 80 | - | 19.4064 | 17.6941 | 17.6941 | 20.9589 | 35 | 35 | 50 | 35 | 33 | - | - | - | - | - | - |  | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 80 | 80 | 35.8846 | 75.8846 | 75.8846 | - | 19.4064 | 17.6941 | 17.6941 | 20.9589 | 34.02 | 33.8455 | 47.8523 |  | 33 | - | - | - | - | - | - |  | - | - | - | - | - | - | -
Ramping (% per minute) | 3 |  | 50 | 50 | - | 50 | - | - | - | - | - | - | - | 50 | - | 3.5 | 4 | 5 | 3 | 20 | 20 | 4 | 20 | 3 | 10 | 20 | 10 |  | 25
Minimum load (% of full load) |  |  | 0 | 0 | - | 0 | - | - | - | - | - | - | - | 0 | - | 30 | 25 | 30 | 50 | 45 | 20 | 30 | 45 | 50 | 30 | 20 | 20 |  | 6
Warm start-up time (hours) |  |  | 0.1 | 0.1 | - | 0.1 | - | - | - | - | - | - | - | 0.1 | - | 3 | 4 | 4 | 6 | 2 | 0.25 | 4 | 2 | 6 | 0.5 |  | 0.5 |  | 0.05
Cold start-up time (hours) |  |  | 0.1 | 0.1 | - | 0.1 | - | - | - | - | - | - | - | 0.1 | - | 8 | 12 | 12 | 15-80 | 4 | 0.5 | 12 | 4 | 15-80 | 10 |  | 2 |  | 0.3
PM 2.5 (gram per Nm3) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 19.6
SO2 (degree of desulphuring, %) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 73 | 73 | 99 | - | - | 97 | 99 | 99 | 0 |  |  |  | 0
NOX (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.5 | 262.5 | 262.5 | 173 | 86.4 | 86.4 | 263 | 80 | 173 | 125 |  |  |  | 280
CH4 (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - |  | - | - |  | - |  | 0.94
N2O (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - |  | - | - |  | - |  | 1.1
Nominal investment (M$/MWe) | 4 | 5 | 2.08 | 2.29 | 2.7 | 0.86 |  |  |  |  | 1.5 | 4 | 3.5 | 5.5 | 5.3 | 1.65 | 1.4 | 1.5248 | 2.4 | 0.69 | 0.7728 | 1.95 | 1.15 | 0.95 | 2 | 2.15 |  | 2.5 | 0.8
- of which equipment | 0.6 | 0.6 | 0.3 | 0.3 | 0.3 |  | 0.44444 | 0.44444 | 0.44444 | 0.50617 | 0.65 | 0.55 | 0.45 |  | 0.87 | [9 empty] | 65 | 65 | 4.012 | 0.72
- of which installation | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 |  | 0.55556 | 0.55556 | 0.55556 | 0.49383 | 0.35 | 0.45 | 0.55 |  | 0.13 | [9 empty] | 35 | 35 | 2.788 | 0.28
Fixed O&M ($/MWe/year) | 50000 | 65000 | 37700 | 41900 | 53000 | 8000 | 14400 | 14400 | 14400 | 16200 | 60000 | 73200 | 72600 | 70800 | 283000 | 45300 | 41200 | 56600 | 60000 | 23500 | 23200 | 41800 | 9000 | 8900 | 47600 | 97000 | 243700 | 125000 | 8000
Variable O&M ($/MWh) | 0.25 | 0.37 | 0.65 | 0.5 | 0.5 | 1.325 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 11.7257 | 0.125 | 0.12 | 0.11 | 12 | 2.3 |  | 3.1 | 1.2 | 5.3 | 3.043 | 0.11 | 24.1437 | 13.5 | 6.4
Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 110 | 50 | 50 | 100 | 80 | 24
2050 | Geothermal - large | Geothermal - small | Large hydro power plant | Medium-small hydro power plant | Mini-micro hydro power plant | Hydro pumped storage | Ground-mounted PV | Rooftop PV | Industrial PV | Floating PV | Wind Onshore | Small wind onshore | Wind Offshore | Tidal Impoundment | Tidal Stream | Coal Subcritical | Coal Supercritical | Coal Ultra supercritical | IGCC | CCGT | SCGT | CCS - Supercritical coal | CCS - CCGT | CCS - IGCC | Biomass power plant (small) | Biogas power plant (small) | MSW incineration | Landfill | Diesel power plant | Batteries
Generating capacity for one unit (MWe) | 55 | 10 | 150 | 50 | 5 | 250 |  |  |  |  | 3.5 | 0.85 | 8 | 1 | 1 | 150 | 600 | 1000 | 150-200 | 600 | 50 | -60 | -40 | -65 | 25 | 1 | 21.5896 | 1 | 20
Generating capacity for total power plant (MWe) | 110 | 20 | 150 | 50 | 5 | 1000 |  |  |  | 10 | 70 | 12.75 | 240 | 30 | 10 | 150 | 600 | 1000 | 600 | 600 | 100 | -60 | -40 | -65 | 25 | 1 | 21.5896 | 1 | 100
Electricity efficiency, net (%), name plate | 16 | 10 | 95 | 95 | 80 | 80 | - | - | - | - | 100 | 100 | 100 | 90 | 90 | 34.83 | 37.67 | 42.5 | 42 | 57 | 33.5 | -7 | -7 | -7 | 32 | 35 | 0.29 | 35 | 46
Electricity efficiency, net (%), annual average | 15 | 10 | 95 | 95 | 80 | 80 | - | - | - | - | 100 | 100 | 100 | 90 | 90 | 34.33 | 36.67 | 41.5 | 40 | 56 | 32.5 | -8 | -8 | -8 | 31 | 34 | 0.2755 | 34 | 45
Forced outage (%) | 10 | 10 | 4 | 4 | 4 | 4 | - | - | - | - | 0.025 | 0.03 | 0.04 | 0.04 | 0.04 | 7 | 7 | 7 | 5.53 | 5 | 2 | 7 | 5 | 6 | 7 | 5 | 0.01 | 5 | 3 | 0.38
Maintenance rate (%) |  | 7.6923 | 11.5385 | 11.5385 | 11.5385 | 5.7692 | #VALUE! | #VALUE! | #VALUE! | #VALUE! | 0.30769 | 0.30769 | 0.30769 | 0 | 0 | 11.5385 | 13.4615 | 13.4615 | 12.6923 | 9.6154 | 5.7692 | 0 | 0 | 0 | 11.5385 | 9.6154 | 5.5769 | 9.6154 | 1.5385 | 0.38462 | 0
Planned outage (weeks per year) | 4 | 4 | 6 | 6 | 6 | 3 | - | - | - | - | 0.16 | 0.16 | 0.16 |  |  | 6 | 7 | 7 | 6.6 | 5 | 3 |  |  |  | 6 | 5 | 2.9 | 5 | 0.8 | 0.2
Technical lifetime (years) | 30 | 30 | 50 | 50 | 50 | 50 | 35 | 35 |  |  | 27 | 27 | 27 | 40 | 25 | 30 | 30 | 30 | 30 | 25 | 25 |  | - | - | 25 | 25 | 25 | 25 | 25 | 20
Construction time (years) | 2 | 2 | 4 | 3 | 2 | 4.3 | 0.5 | 0.1 |  |  | 1.5 | 1 | 3 | 5 | 3 | 3.25 | 3.75 | 4.33 | 4 | 2.5 | 1.5 |  |  |  | 2 | 1.5 | 2.5 | 1.5 | 1 | 0.2
Space requirement (1000 m2/MWe) | 30 | 30 | 62 | 14 |  | 30 |  |  | 9 | 14 | 14 | 58 | 185 | 0.2 |  | - | - | - | - | - | 0.02 |  |  | - | 35 | 70 | 1.5 |  | 0.05
Capacity factor (%), theoretical | 90 | 90 | 40 | 80 | 80 | - | 19.4064 | 17.6941 | 17.6941 | 20.9589 | 35 | 35 | 50 | 35 | 33 | - | - | - | - | - | - |  | - | - | - | - | - | - | -
Capacity factor (%), incl. outages | 80 | 80 | 35.8846 | 75.8846 | 75.8846 | - | 19.4064 | 17.6941 | 17.6941 | 20.9589 | 34.02 | 33.8455 | 47.8523 |  | 33 | - | - | - | - | - | - |  | - | - | - | - | - | - | -
Ramping (% per minute) | 3 |  | 50 | 50 | - | 50 | - | - | - | - | - | - | - | 50 | - | 3.5 | 4 | 5 | 3 | 20 | 20 | 4 | 20 | 3 | 10 | 20 | 10 |  | 25
Minimum load (% of full load) |  |  | 0 | 0 | - | 0 | - | - | - | - | - | - | - | 0 | - | 30 | 25 | 30 | 50 | 45 | 20 | 30 | 45 | 50 | 30 | 20 | 20 |  | 6
Warm start-up time (hours) |  |  | 0.1 | 0.1 | - | 0.1 | - | - | - | - | - | - | - | 0.1 | - | 3 | 4 | 4 | 6 | 2 | 0.25 | 4 | 2 | 6 | 0.5 |  | 0.5 |  | 0.05
Cold start-up time (hours) |  |  | 0.1 | 0.1 | - | 0.1 | - | - | - | - | - | - | - | 0.1 | - | 8 | 12 | 12 | 15-80 | 4 | 0.5 | 12 | 4 | 15-80 | 10 |  | 2 |  | 0.3
PM 2.5 (gram per Nm3) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 19.6
SO2 (degree of desulphuring, %) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73 | 73 | 73 | 99 | - | - | 97 | 99 | 99 | 0 |  |  |  | 0
NOX (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 262.5 | 262.5 | 262.5 | 173 | 86.4 | 86.4 | 263 | 80 | 173 | 125 |  |  |  | 280
CH4 (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - |  | - | - |  | - |  | 0.94
N2O (g per GJ fuel) | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | - | - |  | - | - |  | - |  | 1.1
Nominal investment (M$/MWe) | 4 | 5 | 2.08 | 2.29 | 2.7 | 0.86 |  |  |  |  | 1.5 | 4 | 3.5 | 5.5 | 5.3 | 1.65 | 1.4 | 1.5248 | 2.4 | 0.69 | 0.7728 | 1.95 | 1.15 | 0.95 | 2 | 2.15 |  | 2.5 | 0.8
- of which equipment | 0.6 | 0.6 | 0.3 | 0.3 | 0.3 |  | 0.44444 | 0.44444 | 0.44444 | 0.50617 | 0.65 | 0.55 | 0.45 |  | 0.87 | [9 empty] | 65 | 65 | 4.012 | 0.72
- of which installation | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 |  | 0.55556 | 0.55556 | 0.55556 | 0.49383 | 0.35 | 0.45 | 0.55 |  | 0.13 | [9 empty] | 35 | 35 | 2.788 | 0.28
Fixed O&M ($/MWe/year) | 50000 | 65000 | 37700 | 41900 | 53000 | 8000 | 14400 | 14400 | 14400 | 16200 | 60000 | 73200 | 72600 | 70800 | 283000 | 45300 | 41200 | 56600 | 60000 | 23500 | 23200 | 41800 | 9000 | 8900 | 47600 | 97000 | 243700 | 125000 | 8000
Variable O&M ($/MWh) | 0.25 | 0.37 | 0.65 | 0.5 | 0.5 | 1.325 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5 | 0 | 11.7257 | 0.125 | 0.12 | 0.11 | 12 | 2.3 |  | 3.1 | 1.2 | 5.3 | 3.043 | 0.11 | 24.1437 | 13.5 | 6.4
Start-up costs ($/MWe/start-up) | - | - | - | - | - | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 110 | 50 | 50 | 100 | 80 | 24

## Sources_overview
Origin | Where | Name | Main coverage | Source | Year
Intertek APTECH/NREL | US | Power Plant Cycling Costs | Startup and ramping costs | https://www.nrel.gov/docs/fy12osti/55433.pdf | 2012
GADS | US |  | planned and forced outages+MTTRs+?? | http://gadsopensource.com/Installer.aspx | regular updates?
GADS | US | GADS generating unit statistical Brochure 1 2016 - Units reporting events | outages | http://www.nerc.com/pa/RAPA/gads/_layouts/xlviewer.aspx?id=/pa/RAPA/gads/Reports/Generating%20Unit%20Statistical%20Brochure%201%202016%20-%20Units%20Reporting%20Events.xlsx&Source=http%3A%2F%2Fwww%2Enerc%2Ecom%2Fpa%2FRAPA%2Fgads%2FPages%2FReports%2Easpx&DefaultItemOpen=1 | 2016
NREL | US | Annual Technology Baseline | M&FO but no MTTR, heat rate, MSL | https://atb.nrel.gov/ | annual (2017)
Parsons-Brinckerhoff/Department of Energy and Climate Change | UK | Electricity Generation Cost Model - 2013 Update of Non-renewable technologies | LHV, availability, capacity, VOM | https://www.gov.uk/government/uploads/system/uploads/attachment_data/file/223634/2013_Update_of_Non-Renewable_Technologies_FINAL.pdf | 2013
Ricardo-AEA/EC DG Energy |  | Review of the reference values for high efficiency cogeneration | CHP | https://ec.europa.eu/energy/sites/ener/files/documents/review_of_reference_values_final_report.pdf | 2015
Acil Allen/AEMO | Australia | Fuel and Technology Cost review data | Startup costs, VOM, Maintenance, ramp rates, MSL | https://www.aemo.com.au/-/media/Files/XLS/Fuel_and_Technology_Cost_Review_Data_ACIL_Allen.xlsx | 2014